## NWG 2020 EDM RETURN
Water Company Name | Site Name | Permit No. | Activity Reference (if more than one discharge) on permit | Shellfishery (Only populate for storm overflows that have Shellfish water EDM requirements) | Bathing Beach (Only populate for storm overflows that have bathing water EDM requirements) | Total Duration (hours) of all spills prior to processing through 12-24 hour counting method | Counted spills using 12-24hr counting method | % of reporting period EDM operational | Comments
Northumbrian Water | 1 North Road CSO | 235/1505 |  |  |  | 0.25 | 1 | 99.99%
Northumbrian Water | 223 Geneva Road CSO | Permit Anomaly |  |  |  | 5.25 | 3 | 99.21% | Permit anomaly to be corrected.
Northumbrian Water | 28 Beweshill Crescent CSO | 233/1082 |  |  |  | 0.033333 | 1 | 99.24%
Northumbrian Water | 29/30 North Road CSO | Permit Anomaly |  |  |  | 0.5 | 1 | 81.56% | Comms. failed 19/11/20-end of year. Traffic management required and due to Christmas embargo it couldn't be arranged before 2021. Permit anomaly to be corrected.
Northumbrian Water | 33 Dock Road CSO | 210/1345 |  |  | Spittal | 43.8 | 30 | 99.99%
Northumbrian Water | 46 Burnside Avenue CSO (SU074) | 245/1318 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | 50 Woodside Gardens CSO | 245/1309 |  |  |  | 31.25 | 15 | 99.82%
Northumbrian Water | 66 Ross Lea CSO | 245/1370 |  |  |  | 68 | 36 | 99.73%
Northumbrian Water | A1068 Road Bridge CSO | 223/0871 |  |  | Warkworth & Amble Links | 13.2 | 21 | 99.59%
Northumbrian Water | A66 Rider Sewer | 254/0937 |  |  |  | 8.75 | 8 | 99.97%
Northumbrian Water | A690 Slip Road CSO (SU27) | 245/1357 |  |  |  | 7.5 | 11 | 97.2%
Northumbrian Water | A692 CSO (DER122) | 234/1117 |  |  |  | 18.5 | 18 | 97.34%
Northumbrian Water | Abattoir Street CSO | 254/1860 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Abbey Court (Ampleforth Ave) CSO | 254/1855 |  |  |  | 12 | 9 | 99.73%
Northumbrian Water | Acklam Road CSO | 25/04/1673 | 25/04/1673-01 |  |  |  |  | 0% | Unmonitored in 2020. Monitor recently installed currently in acceptance phase.
Northumbrian Water | Acklam Street SPS | QR.25/04/1512 | QR.25/04/1512-01 |  |  | 8.4414 | 16 | 100%
Northumbrian Water | Acomb Crescent (Cathedral) CSO | 235/1609 |  |  |  | 12.5 | 8 | 99.9%
Northumbrian Water | Acomb CSO | 233/G/0243 |  |  |  | 97.1625 | 69 | 99.54% | Changed to 2 minute logging 18/05/20.
Northumbrian Water | Acomb SPS | 233/1041 | 233/1041-01 |  |  | 76.6069 | 31 | 99.99%
Northumbrian Water | Adderlane School CSO (TD035) | 233/1249 |  |  |  | 15.6333 | 6 | 99.99%
Northumbrian Water | Addison Village CSO | 233/1023 | [5 empty] | 0% | Faulty unit. Maintenance job raised.
Northumbrian Water | Ainsley Street CSO | NPSWQD002839 |  |  |  | 0 | 0 | 99.21%
Northumbrian Water | Aislaby Quay SPS | 254/1928 | A1 |  |  | 18.75 | 4 | 96.35%
Northumbrian Water | Albany Road/Saltmeadows Road CSO | 235/1659 |  |  |  | 20.6 | 24 | 99.99%
Northumbrian Water | Albion Terrace Storm Retention | 255/1092 |  |  |  | 0 | 0 | 100%
Northumbrian Water | Aldbrough SPS | 25/02/1081 | 25/02/1081-01 |  |  | 1115.7489 | 90 | 98.14% | Point upgraded from 01/12/20.
Northumbrian Water | Aldbrough STW | 25/02/1079 | 25/02/1079-03 |  |  | 0 | 0 | 100%
Northumbrian Water | Aldin Grange (North) STW | 244/0991 | 244/0991-03 |  |  | 560.3328 | 75 | 100% | Point upgraded from 26/11/20.
Northumbrian Water | Aldin Grange CSO | 244/1004 |  |  |  | 104 | 37 | 98.98%
Northumbrian Water | Allendale STW | 232/1118 | 232/1118-03 |  |  | 3378.0033 | 176 | 99.99%
Northumbrian Water | Allensway CSO | 254/1382 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Aln Bank CSO | 222/0865 | [5 empty] | 0% | Unmonitored at present. Highlighted on the change control form.
Northumbrian Water | Alnmouth Road CSO | 222/D/0255 |  |  |  | 35.75 | 24 | 97.92%
Northumbrian Water | Alnmouth SPS | 222/0839 | 222/0839-01 |  |  | 24.9181 | 14 | 100%
Northumbrian Water | Alnwick Castle CSO (A011) | 222/0857 |  |  |  | 105 | 68 | 96%
Northumbrian Water | Alnwick Castle CSO No 2 A035 | 222/0827 |  |  |  | 35 | 32 | 99.77%
Northumbrian Water | Alnwick STW - CSO Inlet | 222/0862 | 222/0862-03 |  |  |  |  | 0% | Monitor present, although data is not to our reporting standard and an investigation in place to address matter.
Northumbrian Water | Alnwick STW - Storm Tank | 222/0862 | 222/0862-02 |  |  | 379.9453 | 46 | 100% | Digital point used for the first 6 months of the year as the analogue flow meter was out of operation until July. Possible over reporting from the digital monitor.
Northumbrian Water | Alston Ejector Station CSO | 232/1135 | A1 |  |  | 39.25 | 15 | 96.66%
Northumbrian Water | Amble Harbour SPS | 223/0933 | 223/0933-01 |  | Warkworth & Amble Links | 66.0114 | 26 | 99.99% | Point upgraded from 02/12/20.
Northumbrian Water | Amble Sewage STW | 223/0931 | 223/0931-03 |  |  | 590.2931 | 72 | 98.77% | Installed 30/03/20
Northumbrian Water | Amelia Close C49/102 | 235/1316 |  |  |  | 8.0019 | 18 | 100%
Northumbrian Water | Angate Street CSO | EPRBB3992AT |  |  |  | 0 | 0 | 99.97%
Northumbrian Water | Anick CSO (TD006) | 233/1242 |  |  |  | 49.75 | 22 | 99.86%
Northumbrian Water | Anick Grange SPS CSO & EO | 233/1046 | 233/1046-01 |  |  | 83.3219 | 15 | 99.98%
Northumbrian Water | Annfield Plain CSO | EPRBB3491WR |  |  |  | 13.5 | 5 | 97.65%
Northumbrian Water | Annitsford Bridge CSO | 226/1261 |  |  |  | 0.25 | 1 | 99.99%
Northumbrian Water | Argyle Court CSO | EPRBP3427GC |  |  |  | 1 | 3 | 99.99%
Northumbrian Water | Armonside Road/Connolly Terrace | 234/1124 |  |  |  | 120 | 28 | 96.89%
Northumbrian Water | Ash Meadows CSO | 245/E/0593 |  |  |  | 111.25 | 58 | 99.09%
Northumbrian Water | Ash Tree Lane CSO | 234/1056 |  |  |  | 39.25 | 26 | 99.72%
Northumbrian Water | Ashington CSO Park Road WK 006 | 225/1029 |  |  |  | 17 | 8 | 99.85%
Northumbrian Water | Ashington Drive CSO At Half Moon Roundabout | 225/0940 |  |  |  | 5 | 11 | 89.79% | Comms. failed 12/11/20-14/12/20. Was visited on 30/11/20 but this didn't restore comms.
Northumbrian Water | Ashkirk Way CSO (BV004) | 226/1274 |  |  |  | 15.25 | 14 | 95.65%
Northumbrian Water | Askrigg Street CSO | 253/1088 |  |  |  | 0 | 0 | 98.51%
Northumbrian Water | Atherstone Drive CSO (L022) | 256/1044 |  |  |  | 28.5 | 10 | 99.87%
Northumbrian Water | Atherton Street CSO | 245/1321 |  |  |  | 0.5 | 2 | 99.99%
Northumbrian Water | Atkinson Road CSO | 235/1315 |  |  |  | 27.94 | 34 | 100%
Northumbrian Water | Attwood Terrace CSO (SE008) | 243/1002 |  |  |  | 2.5 | 8 | 95.28%
Northumbrian Water | Avondale CSO | 222/B/0049 |  |  |  | 9.5 | 15 | 98.55%
Northumbrian Water | Aycliffe Avenue CSO | 235/1955 |  |  |  | 30.25 | 22 | 90.86%
Northumbrian Water | Aycliffe STW - Tanks 1-6 Outlet 2 | 253/1278 | A2 |  |  | 99.3544 | 18 | 100%
Northumbrian Water | Aycliffe STW - Tanks 7-9 Outlet 3 | 253/1278 | A2 |  |  | 328.9497 | 25 | 100%
Northumbrian Water | B1285 Storage Tank CSO | 255/1181 |  |  |  | 0 | 0 | 99.87%
Northumbrian Water | B6302 Cornsay Colliery CSO | 244/0921 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Back Elm Street CSO | 244/E/0216 |  |  |  | 9.75 | 9 | 99.69%
Northumbrian Water | Back Lane CSO | 245/1396 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Back Lodge Terrace CSO | 255/1207 |  |  |  | 114 | 43 | 99.99%
Northumbrian Water | Balder Cottage CSO | 251/0925 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Bank Top CSO | 226/1181 |  |  |  | 69.75 | 37 | 99.99%
Northumbrian Water | Barclays A CSO. Elvet | 245/0447 |  |  |  | 0 | 0 | 99.98%
Northumbrian Water | Bardon Mill (The Larches) SPS | 232/0990 | 232/0990-01 |  |  | 0 | 0 | 99.88% | Installed 05/02/20
Northumbrian Water | Bardon Mill (Tow House) SPS | 232/0991 | 232/0991-01 |  |  | 212.9258 | 72 | 99.94%
Northumbrian Water | Barkers Haugh CSO 3 - Court Lane West | 245/E/0659 |  |  |  | 0.25 | 1 | 99.99%
Northumbrian Water | Barkers Haugh CSO 5 - Prebends Bridge | EPRNB3092AL |  |  |  | 1.75 | 5 | 98.88%
Northumbrian Water | Barkers Haugh CSO 8 - Freemans Place | EPRQB3897RB |  |  |  | 336.25 | 91 | 99.59%
Northumbrian Water | Barkers Haugh CSO No 10 - Orchard Drive | EPRJB3293AU |  |  |  | 66.5 | 31 | 99.61%
Northumbrian Water | Barkers Haugh STW | 245/1245 |  |  |  | 1075.71/822.33 | 84/74 | 100%/99.58% | Multiple meters on tanks for a single discharge activity. Investigation into a single meter to be conducted.
Northumbrian Water | Barnard Castle STW - CSO Inlet | 25/02/1111 | 25/02/1111-03 |  |  | 21.38 | 7 | 97.65% | Installed 24/04/20
Northumbrian Water | Barnard Castle STW - Storm Tank | 25/02/1111 | 25/02/1111-02 |  |  | 28.2156 | 10 | 99.57% | Installed 24/04/20
Northumbrian Water | Barningham Sewage Disposal Works | 252/E/0273 |  |  |  | 8.8419 | 17 | 98.98% | Installed 01/05/20
Northumbrian Water | Barrington St CSO | 243/0930 |  |  |  | 29.75 | 27 | 99.96%
Northumbrian Water | Barton STW - CSO Inlet | 25/02/1080 | 25/02/1080-03 |  |  |  |  | 0% | Unmonitored at present. Information suggests this does not spill. Investigation in place to conclude this matter.
Northumbrian Water | Barton STW - Storm Tank | 25/02/1080 | 25/02/1080-02 |  |  | 1147.5642 | 76 | 99.99% | Point upgraded from 25/11/20.
Northumbrian Water | Barwick Street CSO | 255/1126 |  |  |  | 3.75 | 12 | 89.55% | Suffered from water ingress and connection between sensor and logger became corrupt. Therefore the logger sent no data back, but dialled in. Difficult to identify these issues, and problem is persistent. Issue between 23/11/20-end of year.
Northumbrian Water | Bates Colliery SPS | 226/1178 | 226/1178-02 |  |  | 346.7417 | 49 | 100%
Northumbrian Water | Beacon Avenue SPS | 253/0237 | 253/0237-01 |  |  | 1 | 1 | 99.99%
Northumbrian Water | Beadnell (Swinhoe Road) SPS | 221/1070 | 221/1070-01 |  | Beadnell | 0.81667 | 2 | 100% | Point upgraded from 02/12/20.
Northumbrian Water | Beadnell Car Park SPS | 221/1071 | 221/1071-01 |  | Beadnell | 52.3328 | 20 | 100% | There is a shared spill point to the environment with Beadnell Harbour SPS overflow.
Northumbrian Water | Beadnell Harbour SPS | 221/1072 | 221/1072-01 |  | Beadnell | 52.3328 | 20 | 100%
Northumbrian Water | Beal Bank PS & CSO | 223/B/0222 | 223/B/0222-01 |  | Warkworth & Amble Links | 13.4667 | 12 | 87.4% | Low operability due to inability to repair old Cello and unavailability of Point Blue stock due to technical issues surrounding new tender. Now repaired. Unit comms. failed 19/05/20-26/05/20 and 29/05/20-05/06/20 then intermittently between 27/07/20-06/08/20. Failed again 26/08/20-15/09/20 which is when the Point Blue was installed.
Northumbrian Water | Beamish CSO | EPRBB3395WB |  |  |  | 0 | 0 | 99.21%
Northumbrian Water | Beaumont Hill CSO | 25/03/1248 |  |  |  | 5.25 | 10 | 99.99%
Northumbrian Water | Beaumont Wood CSO | 233/1091 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Bebside CSO | 226/1206 |  |  |  | 61.75 | 26 | 99.92%
Northumbrian Water | Bedesway CSO | 235/1276 |  |  |  | 140.3369 | 36 | 100%
Northumbrian Water | Bedford Street CSO (NTY057) | 235/1910 |  |  |  | 21.75 | 20 | 99.4%
Northumbrian Water | Bedlington (Nedderton) CSO | 226/1266 |  |  |  | 18 | 13 | 68.97% | Comms. failed 15/07/20-21/07/20. Following conversion to Point Blue issue with lost comms. 29/07/20-15/09/20 and partial data transfer from 07/10/20-19/11/20.
Northumbrian Water | Beech Hill CSO | 233/D/0390 |  |  |  | 0.23333 | 2 | 99.99%
Northumbrian Water | Beech Street CSO | 234/1058 |  |  |  | 1 | 4 | 99.99%
Northumbrian Water | Beechville CSO | 245/1083 |  |  |  | 192.1167 | 52 | 96.22% | Set to 2 minutes to resolve data spikes. Site visited 23/07/20 by contractor but accidentally left on 15 minute logging until 27/08/20. As permit doesn't require 2 minute logging on this site the operability for this period is calculated against 15 minute expectation.
Northumbrian Water | Beehive CSO | 226/1271 |  |  |  | 73.5 | 30 | 99.29%
Northumbrian Water | Belford Industrial Estate SPS | 221/0934 | 221/0934-02 |  |  | 0 | 0 | 100% | Point upgraded from 26/11/20.
Northumbrian Water | Belford STW - CSO Inlet | 221/1034 | 221/1034-03 |  |  | 510.9883 | 64 | 100%
Northumbrian Water | Belford STW - Storm Tank | 221/1034 | 221/1034-02 |  |  | 495.5111 | 58 | 100%
Northumbrian Water | Bell Burn Wood CSO WV042 (Binchester Blocks) | 243/E/0097 |  |  |  | 8.5 | 6 | 99.9%
Northumbrian Water | Bellingham STW | 231/1086 | 231/1086-02 |  |  | 3087.2472 | 166 | 100%
Northumbrian Water | Bellingham Terminal CSO | 231/G/0108 | 231/G/0108-01 |  |  | 161 | 40 | 99.97%
Northumbrian Water | Belmont STW | 245/1246 | 245/1246-03 |  |  | 153.2589 | 21 | 100% | Installed 06/05/20
Northumbrian Water | Bennetts Walk CSO | EPRDP3923XT |  |  |  | 0.48639 | 6 | 99.74%
Northumbrian Water | Bensham CSO | 235/1737 |  |  |  | 9.5 | 6 | 99.68%
Northumbrian Water | Bensham Hospital CSO | 235/2009 |  |  |  | 1.2333 | 6 | 95.2%
Northumbrian Water | Bensham Sidings CSO | 235/1894 | [5 empty] | 0% | Unmonitored at present. Highlighted on the change control form.
Northumbrian Water | Berry Edge Road CSO | 234/1137 |  |  |  | 12.75 | 24 | 98.87%
Northumbrian Water | Berwick SPS No.7 | 210/1351 | 210/1351-01 |  |  | 107.3833 | 49 | 100%
Northumbrian Water | Berwick upon Tweed SPS & CSO (Berwick SPS 4) | 210/1329 | 210/1329-01 |  | Spittal | 13.9 | 12 | 86.37% | Low operability due to inability to repair old Cello and unavailability of Point Blue stock due to technical issues surrounding new tender. Comms. working until Point Blue installed on 16/09/20. Technical issues associated with new tender have resulted in this not being resolved faster.
Northumbrian Water | Berwick upon Tweed STW - Storm Tank | 210/1273 | 210/1273-02 |  | Spittal | 382.8536 | 53 | 99.99%
Northumbrian Water | Beverley Gardens CSO | NPSWQD009328 |  |  |  | 3.25 | 6 | 97.89%
Northumbrian Water | Billingham STW - CSO Inlet | 254/1965 | [5 empty] | 0% | Unmonitored in 2020. Monitor installed 22/02/21 currently in acceptance phase.
Northumbrian Water | Billingham STW - CSO Inlet - High Level Outfall 1 to Greatham Creek | 254/1965 | 254/1965-08 |  |  | 216.4867 | 45 | 100% | The adequate monitoring point used at the inlet weir measures the total number of spills. This currently does not distinguish between which of the two overflow pipes the storm sewage takes, therefore this has been over reported. The new monitors have been scheduled to be installed.
Northumbrian Water | Billingham STW – CSO Inlet - High Level Outfall 2 to Cowbridge Beck | 254/1965 | 254/1965-08 |  |  | 216.4867 | 45 | 100% | The adequate monitoring point used at the inlet weir measures the total number of spills. This currently does not distinguish between which of the two overflow pipes the storm sewage takes, therefore this has been over reported. The new monitors have been scheduled to be installed.
Northumbrian Water | Billingham STW - Storm Tank | 254/1965 | 254/1965-06 |  |  | 571.2286 | 54 | 100% | Point changed to logger from install on 24/11/20.
Northumbrian Water | Binchester Plantation CSO | 243/0967 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Birtley STW - CSO Inlet | 235/1891 | 235/1891-04 |  |  |  |  | 0% | Unmonitored at present. Scheduled to be installed.
Northumbrian Water | Birtley STW - Storm Tank | 235/1891 | 235/1891-03 |  |  | 138.6725 | 24 | 100%
Northumbrian Water | Bishop Middleham STW - Storm Tank | 25/03/1221 | A2 |  |  | 52.55 | 12 | 100%
Northumbrian Water | Bishop Street CSO - M2 Monitoring Point | 25/04/1701 | A2 |  |  | 88.9667 | 46 | 99.94%
Northumbrian Water | Bishop Street CSO - M3 Monitoring Point | 25/04/1701 | A1 |  |  | 59.7333 | 35 | 99.99%
Northumbrian Water | Bishop Street CSO - M4 Monitoring Point | 25/04/1701 | A3 |  |  | 0 | 0 | 99.99%
Northumbrian Water | Bishopton Mill SPS | 25/04/1766 | 25/04/1766-01 |  |  | 239.7039 | 26 | 99.97%
Northumbrian Water | Bishopton Road CSO | 254/1379 |  |  |  | 407.5 | 39 | 99.4%
Northumbrian Water | Bishopton STW | 25/04/1750 | 25/04/1750-02 |  |  | 26.8278 | 18 | 99.99% | Point upgraded from 11/11/20.
Northumbrian Water | Black Horse CSO | 243/1012 |  |  |  | 25 | 25 | 97.65%
Northumbrian Water | Black Lane CSO | 235/1963 |  |  |  | 2.5 | 7 | 94.43%
Northumbrian Water | Blackett Street CSO | 235/1744 |  |  |  | 11.5 | 5 | 99.97%
Northumbrian Water | Blackhall Mill SPS | 234/0918 | 234/0918-01 |  |  | 1.75 | 3 | 99.99%
Northumbrian Water | Bladeside CSO | 241/1098 |  |  |  | 411.5 | 66 | 98.29%
Northumbrian Water | Blakewell CSO | 210/0938 |  |  | Spittal | 15.3333 | 33 | 95.3%
Northumbrian Water | Blanchland STW - CSO Inlet | 234/1069 | C |  |  | 96.8489 | 26 | 100%
Northumbrian Water | Blanchland STW - Storm Tank | 234/1069 | B |  |  | 107.4061 | 17 | 100% | Point upgraded from 25/11/20.
Northumbrian Water | Blaney Row SPS | 235/1727 | 235/1727-01 |  |  | 3.75 | 2 | 97.46%
Northumbrian Water | Blankney Close CSO | 256/1045 |  |  |  | 5.25 | 3 | 97.21%
Northumbrian Water | Blaydon Bank CSO | 235/1438 |  |  |  | 78.2 | 52 | 99.92%
Northumbrian Water | Blaydon Burn Wagonway CSO | 233/1228 |  |  |  | 23.6533 | 5 | 99.73%
Northumbrian Water | Blaydon Metals No.1 CSO | 235/1685 |  |  |  | 21.9333 | 20 | 99.99%
Northumbrian Water | Blaydon Metals No.2 CSO | 235/1686 |  |  |  | 67.1 | 24 | 99.72%
Northumbrian Water | Bleach Green Farm CSO | 244/0999 |  |  |  | 4.25 | 9 | 99.98%
Northumbrian Water | Blue Bell Inn CSO | 235/1973 |  |  |  | 14.25 | 8 | 99.72%
Northumbrian Water | Bluehouse Gill CSO | 255/1075 |  |  | Crimdon | 828.9528 | 80 | 100%
Northumbrian Water | Blyth No 5 SPS | 226/1176 | 226/1176-02 |  |  | 548.0111 | 49 | 96.44%
Northumbrian Water | Blyth No 6 SPS | 226/1177 | 226/1177-02 |  |  | 37.9975 | 104 | 99.06%
Northumbrian Water | Blyth STW | 226/1179 | A2 |  |  | 914.9783 | 108 | 100%
Northumbrian Water | Boathouse Lane CSO No2 | 254/1366 | A |  |  | 56.5369 | 32 | 100%
Northumbrian Water | Bodlewell Lane CSO | 245/0983 |  |  |  | 102.25 | 39 | 89.4% | Comms. failed 24/11/20-end of year. Was visited on 01/12/20 however battery in old unit had failed, so stock of new unit required. Visited on 06/01/20 but levels were high in chamber due to rainfall.
Northumbrian Water | Boldon Colliery Fenwick Street No 56 CSO | EPRCB3096NZ |  |  |  | 0 | 0 | 94.91% | Installed 15/12/20
Northumbrian Water | Boldon Colliery South Crescent CSO | EPRCB3096RW |  |  |  | 0.5 | 2 | 80.47% | Poor comms. since switch to Point Blue. Failed 01/09/20-28/09/20, 06/11/20-11/11/20 & 18/11/20-12/12/20.
Northumbrian Water | Boldron Sewage Disposal Works | 252/E/0339 |  |  |  | 0.37611 | 1 | 97.54% | Installed 24/04/20
Northumbrian Water | Bondisle Way CSO | 241/1090 |  |  |  | 101.5 | 43 | 97.95%
Northumbrian Water | Bothal (The Tunnels) CSO | 225/1068 |  |  |  | 16.5 | 19 | 99.98%
Northumbrian Water | Bothal Cottages CSO | 225/1028 |  |  |  | 0 | 0 | 69.01% | Comms. fine until 01/09/20. Failed until visit on 18/09/20. Comms. failed again on 10/10/20, weren't restored after a visit on 23/10/20, and still not rectified.
Northumbrian Water | Boulmer STW | 221/1035 | 221/1035-03 |  |  | 267.75 | 48 | 99.9%
Northumbrian Water | Bourn Lea CH087 | 245/1376 |  |  |  | 3.8333 | 7 | 99.94% | Set to 2 minutes to resolve data spikes.
Northumbrian Water | Bowburn Bridge SPS | 243/0980 | 243/0980-01 |  |  | 165.5 | 31 | 99.99%
Northumbrian Water | Bowburn STW - CSO Inlet | 243/0970 | A5 |  |  | 0 | 0 | 100%
Northumbrian Water | Bowburn STW - Storm Tank | 243/0970 | A2 |  |  | 83.5794 | 21 | 54.27% | Installed 06/05/20. Logger failed 30/08/20. Maintenance request raised 15/12/20. Visited 17/12/20.
Northumbrian Water | Bowes STW | 25/02/1105 | 25/02/1105-02 |  |  | 177.6944 | 26 | 67.72% | Installed 31/03/20. Logger not yet commissioned hence unvalidated data and due to communication issues low operability.
Northumbrian Water | Bowesfield Lane CSO | 254/1266 |  |  |  | 4.1333 | 4 | 55.95% | Changed to 2 minute logging 18/05/20. Spurious data received from PTI occasionally through out the year reducing operability, but mainly an issue from 27/06/20-27/08/20, 09/09/20-23/09/20 and 20/10/20-end of year. Access issue at site due to electricians being needed to isolate the screens. Still receive alarms and possible to monitor for obstructions, however EDM data poor.
Northumbrian Water | Bradbury STW | 253/1277 | 253/1277-03 |  |  | 26.7225 | 15 | 99.95%
Northumbrian Water | Brafferton CSO - Rear of Hall Garth Hotel | Permit Anomaly |  |  |  | 95.5 | 13 | 93.26% | Permit anomaly to be corrected.
Northumbrian Water | Bran Sands STW | 254/1920 | 254/1920-07 |  |  | 342.3128 | 68 | 99.57%
Northumbrian Water | Brancepeth STW | 243/1024 | 243/1024-02 |  |  | 2673.1617 | 133 | 99.99%
Northumbrian Water | Brandywell CSO | 210/1359 |  |  | Spittal | 22.4667 | 30 | 99.99%
Northumbrian Water | Branxton STWs | 210/A/0487 |  |  |  | 3.2411 | 2 | 99.17% | Installed 01/09/20
Northumbrian Water | Brenda Road CSO | 255/A/0940 |  |  | Seaton Carew (Centre) | 0 | 0 | 99.99%
Northumbrian Water | Brenda Road/Park View CSO | 25/05/5033 |  |  | Seaton Carew (Centre) | 4.2 | 7 | 99.99%
Northumbrian Water | Briardale CSO | NPSWQD000519 |  |  |  | 2.5 | 5 | 99.99%
Northumbrian Water | Briardale Road CSO | 226/1057 |  |  |  | 38.5 | 22 | 99.99%
Northumbrian Water | Bridge End Cottages CSO | 233/1244 |  |  |  | 3.75 | 10 | 99.81%
Northumbrian Water | Bridge End SPS | 226/1078 | 226/1078-01 |  |  | 0.021667 | 1 | 100%
Northumbrian Water | Bridge Street SPS | 25/05/5040 | 25/05/5040-02 |  |  | 0 | 0 | 9.73% | Installed 20/04/20. Logger not yet commissioned hence unvalidated data and due to communication issues low operability.
Northumbrian Water | Brierdene SPS | 235/1241 | 235/1241-2.1 (Storm Sewage) |  | Whitley Bay | 66.8225 | 24 | 100%
Northumbrian Water | Brinkburn Crescent CSO (SU28) | 245/1358 |  |  |  | 2.25 | 6 | 99.99%
Northumbrian Water | Brinkburn CSO | 245/1355 |  |  |  | 0 | 0 | 97.15%
Northumbrian Water | Broad Chare CSO | 235/1919 |  |  |  | 561.4619 | 73 | 70.79% | Regularly suffers from water ingress and connection between sensor and logger becomes corrupt. Therefore the logger sends no data back, but dials in. Issue from 01/01/20-29/01/20 and 17/10/20-end of year. Normally requires Sunday traffic management so delays in maintaining and due to Christmas embargo current issue hasn't been rectified. Attempted entry on 14/01/21 and 15/01/21 but due to sewer levels in rainfall and snow melt it wasn't possible to access.
Northumbrian Water | Broadway Junction Norwood Road CSO | EPRBB3993EE |  |  |  | 0.16667 | 2 | 99.99%
Northumbrian Water | Broadway Road CSO | EPRBB3999AQ |  |  |  | 0.73333 | 3 | 99.99%
Northumbrian Water | Broken Blackwell Scar SPS | QR.252/1015 | A |  |  | 0.53 | 1 | 99.99% | Point changed to logger from install on 04/09/20.
Northumbrian Water | Brooke Avenue (No20) STY049 CSO | EPRBB3792AU |  |  |  | 54.25 | 38 | 97.92%
Northumbrian Water | Broom Park Old Works CSO | 244/0936 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Broomhaugh STW | 233/1200 | 233/1200-03 |  |  | 947.0553 | 130 | 99.95% | Point upgraded from 26/11/20.
Northumbrian Water | Brotton (Millholme Drive) CSO | 25/06/0985 |  |  | Saltburn Pier | 67.8 | 11 | 99.99%
Northumbrian Water | Browney Lane CSO | 244/1003 |  |  |  | 224.5 | 52 | 99.81%
Northumbrian Water | Browney STW | 244/0985 | A2 |  |  | 914.0628 | 70 | 82.65% | Installed 06/05/20. Logger failed 05/10/20. Maintenance request raised 22/10/20. Visited 05/11/20 however issues continued. Rectified 16/11/20.
Northumbrian Water | Browns Bridge CSO | 254/1833 |  |  |  | 53.5 | 10 | 94.15%
Northumbrian Water | Browns Point High Level CSO | 235/1793 |  |  | Cullercoats | 0.28139 | 2 | 100%
Northumbrian Water | Brus SPS | QC.25/05/5021 | A |  |  | 364.0147 | 46 | 100%
Northumbrian Water | Bt41 Main Street CSO | 210/0940 |  |  | Spittal | 43.8667 | 39 | 99.95%
Northumbrian Water | Bullock Steads CSO (NCO42) | 235/1954 |  |  |  | 0 | 0 | 98.23%
Northumbrian Water | Burdon Main Row CSO | 235/2006 |  |  |  | 11.5 | 17 | 99.99%
Northumbrian Water | Burdon Road CSO | 235/1279 |  |  |  | 39.3667 | 19 | 99.99%
Northumbrian Water | Burn Closes CSO | 235/1776 |  |  |  | 591.25 | 100 | 99.49%
Northumbrian Water | Burnhope SPS | 245/A/0575 | 245/A/0575-B(1) Storm Sewage |  |  | 437.75 | 107 | 88.72% | Spurious data received from unit from 03/10/20-20/11/20 dropping operability of unit.
Northumbrian Water | Burnington Drive SPS CSO | Permit Anomaly |  |  |  | 1513.75 | 122 | 96.51% | Permit anomaly to be corrected.
Northumbrian Water | Burnip Road CSO | 255/0509 |  |  | Seaham Hall | 7.7667 | 19 | 99.99%
Northumbrian Water | Burnopfield CSO | 234/1053 |  |  |  | 170.75 | 38 | 99.19%
Northumbrian Water | Burnside CSO | 235/1916 |  |  |  | 0.5 | 3 | 99.99%
Northumbrian Water | Burton Beck CSO | 243/0974 |  |  |  | 31 | 25 | 99.07%
Northumbrian Water | Busty Bank CSO | 234/0951 |  |  |  | 0.25 | 1 | 99.97%
Northumbrian Water | Busty Bank CSO | 234/0992 |  |  |  | 101.75 | 51 | 99.29%
Northumbrian Water | Busty Bank CSO | 234/1016 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Butsfield Lane CSO (DER092) | 244/1011 |  |  |  | 123 | 57 | 97.36%
Northumbrian Water | Butterknowle STW | 242/1070 | A2 |  |  | 2047.2803 | 126 | 100% | Point upgraded from 25/11/20.
Northumbrian Water | Butteryhaugh SPS | 231/0965 | 231/0965-01 |  |  | 311.1389 | 26 | 99.9%
Northumbrian Water | Bydales School CSO | 25/06/1019 |  |  | Marske | 29.2333 | 24 | 99.99%
Northumbrian Water | Byers Green SPS | 243/0959 | 243/0959-02 |  |  | 685.2742 | 65 | 99.91%
Northumbrian Water | Calbeck Close/Belmont St. Anthonys | 235/1324 |  |  |  | 22.0456 | 24 | 100%
Northumbrian Water | Caldbeck Av/Pottery Bank CSO | 235/1325 |  |  |  | 0.35833 | 3 | 100%
Northumbrian Water | Caldbeck Av/Pottery Bank CSO | 235/1326 |  |  |  | 60.3514 | 16 | 100%
Northumbrian Water | Caledonian St / William St D17-103 STY056 | Permit Anomaly |  |  |  | 0 | 0 | 97.67% | Permit anomaly to be corrected.
Northumbrian Water | Calf Fallow Lane SPS | 25/04/1790 | 25/04/1790-01 |  |  | 13.25 | 11 | 99.99%
Northumbrian Water | California Row CSO | 251/0863 |  |  |  | 5.75 | 3 | 99.48%
Northumbrian Water | Cambois STW | 226/1119 | 226/1119-03 |  |  | 62.0875 | 15 | 100%
Northumbrian Water | Car Park CSO | 210/1344 |  |  | Spittal | 31.9667 | 26 | 99.99%
Northumbrian Water | Cargo Fleet Foul SPS | QR.25/04/1514 | [5 empty] | 0% | Monitor installed but data not recovered. Investigation undertaken.
Northumbrian Water | Cargo Fleet Foul SPS | QR.25/04/1514 | 25/04/1514 S2 |  |  | 590.97/590.98 | 69/69 | 100%/100%
Northumbrian Water | Carlton & Redmarshall STW | 25/04/1706 | 25/04/1706-03 |  |  | 900.2131 | 63 | 99.87% | Point upgraded from 11/11/20.
Northumbrian Water | Carlton In Cleveland STW | 25/04/1800 |  |  |  | 182.0814 | 56 | 99.81%
Northumbrian Water | Carlton Village SPS | 254/D/0172 | A1 |  |  | 523.3922 | 49 | 100%
Northumbrian Water | Caroline Street CSO | EPRAB3593AS |  |  |  | 4.25 | 9 | 99.99%
Northumbrian Water | Cassop STW | 243/1016 | 243/1016-02 |  |  | 350.5764 | 54 | 100%
Northumbrian Water | Castle Dene CSO | 245/E/0592 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Castle Square CSO CM020 | 225/F/0525 | [5 empty] | 0% | Unmonitored in 2020. Monitor installed 22/02/21 currently in acceptance phase.
Northumbrian Water | Castle Terrace 1 CSO | 210/1356 |  |  | Spittal | 27.9 | 29 | 99.84%
Northumbrian Water | Castle Terrace No2 (BT341) CSO | WQD000697 |  |  | Spittal | 0 | 0 | 86.28% | Comms. failed 18/11/20-end of year. Was visited on 26/11/20 however comms. weren't restored and contractor needs to return to install new unit.
Northumbrian Water | Castle Vale SPS | 210/1249 | 210/1249-01 |  | Spittal | 0 | 0 | 99.99%
Northumbrian Water | Castleside CSO | 234/1105 |  |  |  | 7.75 | 13 | 94.2%
Northumbrian Water | Castleton Walk CSO | 254/1418 |  |  |  | 10.7667 | 11 | 96.37%
Northumbrian Water | Castletown Way CSO & SPS | 245/0937 | 245/0937-01 |  |  |  |  | 0% | Monitor in place, data under review.
Northumbrian Water | Cathedral Banks CSO | 245/1336 |  |  |  | 0.5 | 2 | 99.99%
Northumbrian Water | Cattle Market B (WV4) CSO | 242/1045 |  |  |  | 882.25 | 87 | 98.37%
Northumbrian Water | Catton Lea CSO | 232/1001 |  |  |  | 0 | 0 | 98.11%
Northumbrian Water | Cauldwell CSO | 234/1087 |  |  |  | 5.25 | 7 | 99.98%
Northumbrian Water | Causey STW | 235/2007 | 235/2007-02 |  |  | 33.1192 | 4 | 100% | Installed 06/08/20
Northumbrian Water | Cemetery Road CSO | 255/1057 |  |  |  | 7.75 | 8 | 68.61% | Intermittent comms. received traditionally at this site. Comms. generally recover after a maintenance visit, however fail shortly afterwards. Site was visited on 08/09/20 to install a Point Blue however comms. failed three days later between 11/09/20-10/12/20. Visit on 05/11/20 didn't restore comms. Comms. then failed again 13/12/20-end of year.
Northumbrian Water | Cemetery Road CSO STY029 | 235/C/0047 |  |  |  | 36.5 | 19 | 95.97%
Northumbrian Water | Chapel Court (DU068) CSO | 245/1081 |  |  |  | 159.5 | 57 | 99.74%
Northumbrian Water | Chapel Street | Permit Anomaly |  |  |  | 2.25 | 6 | 99.99% | Permit anomaly to be corrected.
Northumbrian Water | Chapel Street CSO | 243/0931 |  |  |  | 4.25 | 10 | 98.49%
Northumbrian Water | Chare Bank (Ebchester Hill) CSO | 234/1156 |  |  |  | 130.25 | 37 | 99.93%
Northumbrian Water | Charlaw Terrace CSO | 245/1071 |  |  |  | 0.23333 | 7 | 99.99% | Set to 2 minutes to resolve data spikes.
Northumbrian Water | Charlton Village CSO | 25/06/1026 |  |  |  | 0.75 | 3 | 99.98%
Northumbrian Water | Chatton CSO | NPSWQD006661 |  |  |  | 3.25 | 6 | 74.63% | Comms. failed 31/10/20-end of year. New Point blue unit that needs revisiting with new firmware. Until this is resolved operability will be poor.
Northumbrian Water | Chatton STW | Permit Anomaly |  |  |  | 215.6325 | 60 | 100% | Installed 21/07/20
Northumbrian Water | Cherry Banks CSO (CH72) | 245/1306 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Chester Le Street STW - Storm Tank | 245/1242 | A2 |  |  | 523.0642 | 48 | 100% | Installed 25/03/20
Northumbrian Water | Chester-Le-Street STW - CSO Inlet | 245/1242 | A3 |  |  | 20.6592 | 9 | 100% | Point upgraded from 17/11/20.
Northumbrian Water | Chilton Lane A CSO | QR.25/03/1097 |  |  |  | 55 | 48 | 99.86%
Northumbrian Water | Chilton Lane B CSO | QR.25/03/1098 |  |  |  | 47.75 | 28 | 99.98%
Northumbrian Water | Chilton Lane SPS | 253/1287 | 253/1287-01 |  |  | 794.9303 | 61 | 100%
Northumbrian Water | Chopwell Park Footpath | 234/1123 |  |  |  | 22.25 | 19 | 99.89%
Northumbrian Water | Chopwell Road CSO | 234/1139 |  |  |  | 37 | 16 | 96.88%
Northumbrian Water | Chowdene CSO | 235/F/0655 |  |  |  | 18.5 | 23 | 99.99%
Northumbrian Water | Christon Bank SPS | 221/1030 | 221/1030-01 |  |  | 149.75 | 36 | 99.98%
Northumbrian Water | Church Bank CSO | 235/1777 |  |  |  | 0.34167 | 1 | 100%
Northumbrian Water | Church Dene CSO | 232/1010 |  |  |  | 281.75 | 52 | 89.52% | Poor signal area. Inoperable from 21/01/20-29/01/20 (attended within SLA period). Comms. failed again on 05/04/20. Delay in attending after new contract went live and comms. restored on 30/04/20.
Northumbrian Water | Church Lane (High Street) CSO | 254/1406 |  |  |  | 13 | 13 | 99.92%
Northumbrian Water | Church Lane CSO WV083 | 244/1023 |  |  |  | 23.25 | 10 | 96.14%
Northumbrian Water | Church Road CSO (DER159) | 234/1132 |  |  |  | 51 | 49 | 99.6%
Northumbrian Water | Church Street CSO | 210/1320 |  |  |  | 23.5 | 19 | 93.06%
Northumbrian Water | Church Street DU026 | 245/1388 |  |  |  | 2.25 | 5 | 59.79% | On cross roads on busy road so Sunday traffic management required for comms. failures. Christmas embargo and Durham County Council works on New Elvet Bridge have restricted access. Comms. failed 01/01/20-26/01/20, 01/09/20-end of year.
Northumbrian Water | Church Street No26 CSO | NPSWQD008982 |  |  |  | 46.5 | 38 | 99.96%
Northumbrian Water | Church Vale CSO 1 | 245/E/0065 |  |  |  | 1.75 | 4 | 99.99%
Northumbrian Water | Church Vale CSO 2 | 245/1385 |  |  |  | 0.5 | 2 | 99.99%
Northumbrian Water | Church Villas CSO | 245/1260 |  |  |  | 7.75 | 10 | 95.05%
Northumbrian Water | Clara Vale SPS | 235/1743 | 235/1743-01 |  |  | 85 | 30 | 90.77%
Northumbrian Water | Cleasewell Hill SPS | NPSWQD007427 | NPSWQD007427-01 |  |  | 35.75 | 29 | 75.94% | Regularly suffers from water ingress and connection between sensor and logger becomes corrupt. Therefore the logger sends no data back, but dials in. Difficult to identify these issues, and problem is persistent. Issue between 03/03/20-17/03/20, 23/03/20-12/05/20,02/06/20-05/06/20, 09/06/20-29/06/20.
Northumbrian Water | Cleveland Road CSO | QC.25/05/5016 |  |  |  | 635.25 | 59 | 89.67% | Comms. failure 20/04/20-27/05/20 wasn’t visited in time by contractor, due to traffic management requirement. Resolved first time when attended.
Northumbrian Water | Clifton Lodge CSO | NPSWQD003961 | [5 empty] | 0% | Unmonitored at present. Highlighted on the change control form.
Northumbrian Water | Clockwood SPS | 25/04/1679 | 25/04/1679-03 |  |  | 344.5 | 41 | 99.51% | Incorrectly reported as the wrong schedule in the 2019 return. The data against 25/04/1679-01 last year was for schedule 25/04/1679-03
Northumbrian Water | Clockwood SPS | 25/04/1679 | 25/04/1679-01 |  |  |  |  | 0% | Unmonitored in 2020. Monitor installed 04/02/21 currently in acceptance phase.
Northumbrian Water | Close House (WV29) CSO | 242/1013 |  |  |  | 0 | 0 | 92.59%
Northumbrian Water | Coalford Lane CSO | 245/1343 |  |  |  | 0 | 0 | 96.27%
Northumbrian Water | Coatham Lane CSO (Ref L10) | 254/1914 |  |  |  | 15 | 7 | 99.98%
Northumbrian Water | Cochrane Street CSO | 233/1020 |  |  |  | 0 | 0 | 100%
Northumbrian Water | Cockfield CSO Blackburn Bridge | 242/1056 |  |  |  | 19.75 | 11 | 94.31%
Northumbrian Water | Cockfield Fell No.2 CSO | 242/1054 |  |  |  | 4.5 | 3 | 99.99%
Northumbrian Water | Cockfield STW | 242/1052 | A2 |  |  | 1438.8214 | 74 | 99.99% | Point upgraded from 25/11/20.
Northumbrian Water | Coldwell Burn CSO | 245/0264 |  |  |  | 3 | 4 | 99.99%
Northumbrian Water | Colwell STW | 231/1077 | 231/1077-03 |  |  | 1933.5275 | 84 | 100% | Installed 07/10/20
Northumbrian Water | Colwell STW - CSO Inlet | 231/1077 | 231/1077-04 |  |  | 331.8383 | 33 | 99.22% | Installed 17/04/20
Northumbrian Water | Cone Lane (Chester No 4) CSO | 245/1328 |  |  |  | 1.5 | 4 | 99.99%
Northumbrian Water | Congburn Bank CSO | 245/E/0621 |  |  |  | 0.5 | 2 | 99.85%
Northumbrian Water | Coniscliffe Road CSO | 25/05/5029 |  |  |  | 0 | 0 | 98.47%
Northumbrian Water | Conishead Terrace CSO | 245/A/0605 |  |  |  | 42.25 | 21 | 99.76%
Northumbrian Water | Consett Academy South (DER090) CSO | 234/1154 |  |  |  | 55 | 37 | 99.99%
Northumbrian Water | Consett CSO Fellside Delves Lane | 244/1010 |  |  |  | 27.25 | 17 | 99.98%
Northumbrian Water | Consett OAP Hall CSO | EPRAB3596NY |  |  |  | 0.25 | 1 | 88.19% | Issues with old logger led to maintenance request being raised. Replaced with new contractor's unit however data transfer has been sporadic since due to technical issues with communication between unit and top end SCADA system.
Northumbrian Water | Consett STW | 234/1061 | 234/1061-02 |  |  | 1220.9333 | 147 | 99.95%
Northumbrian Water | Coopers Close CSO | 255/1195 |  |  |  | 0 | 0 | 98.23%
Northumbrian Water | Copeland Estate Off-Site Sewer CSO | 242/E/0382 |  |  |  | 14.75 | 9 | 93.49%
Northumbrian Water | Cormorant Drive CSO | 235/1887 |  |  |  | 121.3 | 28 | 99.58%
Northumbrian Water | Cornfield Road SPS CSO & EO | 254/1805 | 254/1805-01 |  |  | 7 | 5 | 99.99%
Northumbrian Water | Cornforth Lane Roundabout CSO | 243/0986 |  |  |  | 2.75 | 8 | 99.99%
Northumbrian Water | Cornhill SPS | 210/0984 | 210/0984-02 |  |  | 3.1186 | 3 | 99.71% | Point changed to logger from install on 03/12/20.
Northumbrian Water | Coronation Street CSO | EPRBP3720XY |  |  |  | 230.0025 | 37 | 100%
Northumbrian Water | Cotherstone STW | 25/01/0920 | 25/01/0920-02 |  |  | 145.8758 | 21 | 99.08% | Installed 01/09/20
Northumbrian Water | Cotsford Jnr School CSO (EA073) | 255/1212 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Cow Plantation CSO | 243/0973 |  |  |  | 29 | 14 | 94.85%
Northumbrian Water | Cowpen Bewley SPS | 25/04/1785 | A1 |  |  | 163.5 | 25 | 99.93%
Northumbrian Water | Cowpen Road CSO | EPRJB3399NK |  |  |  | 46.5 | 12 | 99.97%
Northumbrian Water | Cox Green SPS | 245/1218 | 245/1218-01 |  |  | 48.0942 | 6 | 99.93%
Northumbrian Water | Craghead CSO Kimberley Gardens (No.24) DER082 | 245/1308 |  |  |  | 136.5 | 53 | 99.64% | Data provided for additional site not identified on the EDM Tracker as requested by REDACTED letter dated 08/02/21.
Northumbrian Water | Craghead Front Street (North) (New) | 245/1331 |  |  |  | 4.75 | 14 | 99.83% | Data provided for additional site not identified on the EDM Tracker as requested by REDACTED letter dated 08/02/21.
Northumbrian Water | Cramlington STW - CSO Inlet | 226/1187 | 226/1187-03 |  |  | 139.3914 | 34 | 100%
Northumbrian Water | Cramlington STW - Storm Tank | 226/1187 | 226/1187-04 |  |  |  |  | 0% | Monitor present, although data is not to our reporting standard and an investigation in place to address matter.
Northumbrian Water | Craster North SPS | 221/0921 | 221/0921-01 |  |  | 2.5867 | 37 | 99.86% | Installed 06/02/20
Northumbrian Water | Craster South SPS | 221/0920 | 221/0920-01 |  |  | 41.4081 | 74 | 99.95% | Installed 06/02/20
Northumbrian Water | Crathorne SPS | QR.25/04/1582 | S1 |  |  | 156.77 | 27 | 99.78%
Northumbrian Water | Cree Beck CSO | NPSWQD005054 |  |  |  | 4.25 | 4 | 99.94%
Northumbrian Water | Cresswell SPS | 224/0986 | A1 |  |  | 19.9219 | 8 | 99.94%
Northumbrian Water | Cricket Ground Holmside Lane CSO | EPRBB3496RP |  |  |  | 1.25 | 5 | 99.99%
Northumbrian Water | Crimdon Park SPS | 255/1115 | 255/1115-3A (Storm Sewage) |  | Crimdon | 34.4667 | 7 | 99.99%
Northumbrian Water | Croft SPS | 254/1018 | A |  |  | 580.2856 | 59 | 100%
Northumbrian Water | Croftdale Road CSO | 235/1437 |  |  |  | 9.5333 | 17 | 99.99%
Northumbrian Water | Crookhall STW - CSO Inlet | 244/1006 | 244/1006-03 |  |  | 47.3317 | 30 | 100% | Point upgraded from 26/11/20.
Northumbrian Water | Crookhall STW - Storm Tank | 244/1006 | 244/1006-02 |  |  |  |  | 0% | Monitor installed 10/03/20 but not commissioned. Investigation to address the matter required.
Northumbrian Water | Crookham STW Inlet CSO | Permit Anomaly |  |  |  | 0 | 0 | 100% | Installed 15/04/20
Northumbrian Water | Cross Lane CSO (CH8) | 245/1283 |  |  |  | 0 | 0 | 88.97% | Following install of new unit comms. have failed 14/11/20-11/12/20 and 21/12/20-end of year.
Northumbrian Water | Cross Street CSO | 243/0916 |  |  |  | 0.75 | 3 | 99.99%
Northumbrian Water | Crossfell SPS | 226/A/0973 | 226/A/0973 (Storm Sewage) |  |  | 0 | 0 | 99.87%
Northumbrian Water | CSO (WV80) Disused STW Hunwick | 243/0910 |  |  |  | 387.25 | 90 | 82.73% | Comms. failed 11/11/20-end of year. Not been visited by contractor since comms. failure. They were informed on 12/11/20.
Northumbrian Water | CSO 200m West of Walton Road | 245/1152 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | CSO 32 Walbottle Road | 235/1876 |  |  |  | 0.56667 | 2 | 99.99%
Northumbrian Water | CSO Adj 40 Hollyhill Gdn | 245/1258 |  |  |  | 60.25 | 42 | 98.49%
Northumbrian Water | CSO at Church Dene | 233/1004 |  |  |  | 1.25 | 4 | 99.99%
Northumbrian Water | CSO at Cromwell Rd | 235/1199 |  |  |  | 11.1672 | 14 | 100%
Northumbrian Water | CSO at Green Lane | 254/1174 |  |  |  | 73.8 | 48 | 99.94%
Northumbrian Water | CSO at Hebburn Riverside | 235/1187 |  |  |  | 3.75 | 2 | 99.45%
Northumbrian Water | CSO at Heugh Road SPS | 221/0918 | A |  |  | 34.7064 | 12 | 99.88% | Adequate regional telemetry monitoring point from the wet well in use. Awaiting an SLM install.
Northumbrian Water | CSO at Heworth Shore | 235/1201 |  |  |  | 3.75 | 2 | 91.82%
Northumbrian Water | CSO at Jonadab | 235/1200 |  |  |  | 11.25 | 15 | 71.15% | Comms. of new unit failed 06/08/20-14/09/20 and again 28/10/20-end of year. Technical issues with new logger will need to be resolved before this is fully functional.
Northumbrian Water | CSO at Manhole A9 Howdon Road | 235/1489 |  |  |  | 1.9072 | 6 | 99.95%
Northumbrian Water | CSO at Nest Road | 235/1203 |  |  |  | 0 | 0 | 99.71%
Northumbrian Water | CSO at Preston Lane | 254/1177 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | CSO at Rear of Orchid Crescent | 235/1204 |  |  |  | 143.7272 | 43 | 100%
Northumbrian Water | CSO at Reyrolle Sewer (North) | 235/1185 | [5 empty] | 0% | Unmonitored at present. Highlighted on the change control form.
Northumbrian Water | CSO at St Peters SPS | 245/1004 | A1 |  |  | 221.3519 | 16 | 100%
Northumbrian Water | CSO at Staithes Road (S) Sewer | 235/1253 |  |  |  | 200.8903 | 43 | 99.98%
Northumbrian Water | CSO at Station Street | 254/1277 |  |  |  | 31.5333 | 31 | 99.99%
Northumbrian Water | CSO at Stoneygate Lane | 235/1202 |  |  |  | 1.0667 | 8 | 99.99%
Northumbrian Water | CSO at Sun Street - M2 | 254/1278 | M2 |  |  | 39.75 | 21 | 99.65%
Northumbrian Water | CSO at Sun Street - M3 | 254/1278 | M3 |  |  | 75 | 27 | 97.57%
Northumbrian Water | CSO at Team Street | 235/1250 |  |  |  | 161.8681 | 18 | 99.98%
Northumbrian Water | CSO at the Wynd SPS | 223/0864 | 223/0864 (Schedule 3A Storm Sewage) |  | Warkworth & Amble Links | 9.1767 | 1 | 99.99%
Northumbrian Water | CSO at West End | 210/0939 |  |  | Spittal | 6.5667 | 11 | 99.99%
Northumbrian Water | CSO Benton Way No.2 Outfall | 235/1626 |  |  |  | 2 | 3 | 93.84%
Northumbrian Water | CSO Blackhills Farm | 255/1151 |  |  |  | 9.25 | 8 | 99.99%
Northumbrian Water | CSO Canterbury Road | 245/1154 |  |  |  | 44.5 | 25 | 99.58%
Northumbrian Water | CSO Caravan Park | 25/06/0983 |  |  | Saltburn Pier | 646.6931 | 40 | 99.9%
Northumbrian Water | CSO Clumber Street | 235/1318 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | CSO Coop House Wood | 255/1135 |  |  | Seaham Beach | 271.9667 | 45 | 99.99%
Northumbrian Water | CSO Cottage Hospital | QR.25/06/0939 |  |  |  | 42.75 | 14 | 99.99%
Northumbrian Water | CSO Dragon Lane | 245/1136 |  |  |  | 0.25 | 1 | 99.99%
Northumbrian Water | CSO Dunn Street | 235/1631 |  |  |  | 58.75 | 32 | 89.45% | Comms. failed 17/11/20-end of year. Site was visited on 25/11/20 however traffic management was required and due to Christmas embargo it couldn't be arranged before 2021.
Northumbrian Water | CSO East Holborn East | 235/1645 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | CSO East Holborn West | 235/1644 |  |  |  | 0.36667 | 1 | 99.9%
Northumbrian Water | CSO East Of Stobbs House View | 244/0952 |  |  |  | 0 | 0 | 99.98%
Northumbrian Water | CSO Fallsway | 245/1160 |  |  |  | 2 | 3 | 98.18%
Northumbrian Water | CSO Forth Banks | 235/1628 |  |  |  | 50.1667 | 29 | 99.98%
Northumbrian Water | CSO Grangetown | 255/1202 |  |  |  | 24.3847 | 21 | 99.98%
Northumbrian Water | CSO Hillerston Terrace | 232/1022 |  |  |  | 226 | 15 | 91.36%
Northumbrian Water | CSO Holmsfoot | 232/1021 |  |  |  | 12.25 | 7 | 99.58%
Northumbrian Water | CSO Horden Burn No.3 | 255/1152 |  |  |  | 0 | 0 | 96.78%
Northumbrian Water | CSO Junction Langholme Avenue & Beckenham Avenue | 235/1590 |  |  |  | 0.75 | 2 | 99.98%
Northumbrian Water | CSO MH 9901 Garrigill | 232/1020 |  |  |  | 47.8333 | 11 | 25.78% | Operability <90% due to poor comms. - The monitor requires a site visit to download the data as it's situated in a remote location with poor network coverage and no electricity supply.
Northumbrian Water | CSO Michel Bearings North | 235/1671 |  |  |  | 0 | 0 | 99.4% | Changed to 2 minute logging 04/03/20.
Northumbrian Water | CSO Neptune Yard No. 1 Outfall | 235/1623 |  |  |  | 2.0117 | 4 | 100%
Northumbrian Water | CSO New Drive Recreation Ground | 255/1154 |  |  | Seaham Hall | 0.63333 | 4 | 99.94%
Northumbrian Water | CSO on the Whickham & Gateshead sewer | 235/1252 |  |  |  | 205.8606 | 48 | 100%
Northumbrian Water | CSO Outside Milkwell Cottages | 233/1246 |  |  |  | 0.25 | 1 | 99.99%
Northumbrian Water | CSO Rear 13 St Austell Gardens | 235/1483 |  |  |  | 0 | 0 | 94.83%
Northumbrian Water | CSO Rear of Aged Miners Homes | 244/0916 |  |  |  | 0 | 0 | 99.86%
Northumbrian Water | CSO Rear of Holly House | 25/05/5038 |  |  |  | 0 | 0 | 99.93%
Northumbrian Water | CSO Redheugh Bridge | 235/1627 |  |  |  | 30.9 | 37 | 99.93%
Northumbrian Water | CSO Riverside Park West | 235/1765 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | CSO Salterfen | 255/1201 |  |  |  | 57.5 | 43 | 99.63%
Northumbrian Water | CSO Seaham Park | 255/1153 |  |  | Seaham Hall | 0 | 0 | 99.99%
Northumbrian Water | CSO Second St | 244/0956 |  |  |  | 0 | 0 | 94.57%
Northumbrian Water | CSO Skelton (Saltburn Lane) | 25/06/0986 |  |  | Saltburn Pier | 32.9383 | 4 | 100%
Northumbrian Water | CSO Sunderland Gas Works | 255/1198 |  |  |  | 4 | 11 | 99.97%
Northumbrian Water | CSO SW of Sheraton STW | 255/1132 |  |  |  | 5.75 | 7 | 99.99%
Northumbrian Water | CSO Three Mile Inn | 235/1725 |  |  |  | 0.5 | 2 | 99.96%
Northumbrian Water | CSO to Rear 1 River Terrace | 25/01/0922 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | CSO to Rear 12 Springwell Close | 25/02/1097 |  |  |  | 4.75 | 6 | 99.68%
Northumbrian Water | CSO to Rear 8 Otterington Close | 25/05/5039 |  |  |  | 44.5 | 21 | 99.99%
Northumbrian Water | CSO to Rear No.48 Market Place | 251/0924 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | CSO to Rear Of 62 Grange Ave | QR.25/04/1563 |  |  |  | 0.25 | 1 | 97.69%
Northumbrian Water | CSO Warkworth Crescent | 255/1157 |  |  |  | 62.25 | 24 | 99.63%
Northumbrian Water | CSO Warkworth Drive | 245/1115 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | CSO Water Street | 235/1632 |  |  |  | 65.6333 | 33 | 99.99%
Northumbrian Water | CSO Welbeck Rd/Bath St | 235/1331 |  |  |  | 91.4333 | 55 | 99.94%
Northumbrian Water | CSO West End | 226/1125 |  |  | Seaton Sluice | 0.1 | 3 | 99.99%
Northumbrian Water | CSO West End Fishburn Terrace | QR.25/03/1100 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | CSO West Lane School | 234/0967 |  |  |  | 12.25 | 5 | 97.18%
Northumbrian Water | CSO Whittonstall | 234/1026 |  |  |  | 0 | 0 | 93.68%
Northumbrian Water | CSO Woodland Road | QR.25/03/1099 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | CSO Yarm Road (Dl18) | 25/03/1214 |  |  |  | 0 | 0 | 97.56%
Northumbrian Water | Cumberland Street CSO | 242/0641 |  |  |  | 40 | 31 | 99.62%
Northumbrian Water | Cutlers Hall Road (No29) Storm | EPRAB3992WX |  |  |  | 37.75 | 14 | 96.71%
Northumbrian Water | Dairy Lane CSO SU024 Sewer | 245/A/0520 |  |  |  | 5 | 4 | 97.07%
Northumbrian Water | Dale Street CSO (Ref.L27) | 25/06/1030 |  |  | Marske | 0.23333 | 3 | 99.99%
Northumbrian Water | Dalton Le Dale CSO (E038) | 255/D/0277 |  |  | Seaham Hall | 350.9 | 56 | 99.94%
Northumbrian Water | Dalton Piercy SPS | 254/1077 | A1 |  |  | 57 | 13 | 99.96%
Northumbrian Water | Dalton Retail Park CSO | EPRBB3793WU | [5 empty] | 0% | Incorrectly classified as a category D on the EDM Tracker and unmonitored presently. Classification to be reviewed and monitor installed.
Northumbrian Water | Daphne Crescent CSO | NPSWQD005830 |  |  |  | 0.25 | 1 | 99.99%
Northumbrian Water | Darlington Brunswick Street CSO | EPRCB3094AD |  |  |  | 95.75 | 18 | 99.65%
Northumbrian Water | Darlington Crown St (No 34) CSO | EPRCB3095WD |  |  |  | 24 | 14 | 98.79%
Northumbrian Water | Darlington CSO Brinkburn Dene Cocker Beck | 253/1921 |  |  |  | 1.25 | 3 | 99.99% | Data provided for additional site not identified on the EDM Tracker as requested by REDACTED letter dated 08/02/21.
Northumbrian Water | Darlington Lane CSO | 25/04/1623 |  |  |  | 9.25 | 13 | 99.99%
Northumbrian Water | Davy Bank SPS | 235/1687 | 235/1687-01 |  |  | 16.5 | 22 | 99.74%
Northumbrian Water | Dean Road CSO (Front of No 35) | EPRBB3495RJ |  |  |  | 1.75 | 6 | 97.92%
Northumbrian Water | Dean Street (High Level) CSO | 235/1921 |  |  |  | 0 | 0 | 97.22% | Installed 20/10/20
Northumbrian Water | Deepdale Avenue CSO | 254/1815 |  |  |  | 6.75 | 8 | 99.99%
Northumbrian Water | Dellwood Pumped Storage Tank CSO | 242/1042 |  |  |  | 1885 | 137 | 99.34%
Northumbrian Water | Demesne Mill CSO (East) | 252/A/0559 |  |  |  | 125.25 | 39 | 95.79%
Northumbrian Water | Demesnes Mill CSO | 252/1124 |  |  |  | 123.75 | 38 | 96.56%
Northumbrian Water | Demesnes Mill No.3 CSO | QC.25/02/1066 |  |  |  | 11.75 | 8 | 98.81%
Northumbrian Water | Dene Avenue CSO (NC051) | 233/1271 |  |  |  | 9.5 | 17 | 99.57%
Northumbrian Water | Dene Hall Drive CSO | EPRCB3290DR |  |  |  | 43.25 | 17 | 99.99%
Northumbrian Water | Dene House SPS | 224/1004 | 224/1004-01 |  |  | 215.0314 | 38 | 100%
Northumbrian Water | Denecrest CSO | 234/0999 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Deneholme Tidal Tank | 255/1148 | 255/1148-01 |  |  |  |  | 0% | Monitor present, although data is not to our reporting standard and an investigation in place to address matter.
Northumbrian Water | Deneholme Tidal Tank | 255/1149 | 255/1149-01 |  |  |  |  | 0% | Monitor present, although data is not to our reporting standard and an investigation in place to address matter.
Northumbrian Water | Deneside | 244/0959 |  |  |  | 35 | 28 | 99.59%
Northumbrian Water | Dent Street | 226/1059 |  |  | Blyth South Beach | 0 | 0 | 96.82%
Northumbrian Water | Denton Dene North of West Road CSO | 235/1869 |  |  |  | 8.6 | 16 | 98.65%
Northumbrian Water | Denton Road CSO (Nco27) | 235/1937 |  |  |  | 367.0064 | 86 | 97.85%
Northumbrian Water | Deptford SPS | 245/1212 | 245/1212-01 |  |  | 195.75 | 46 | 99.98%
Northumbrian Water | Derwent Park Caravan Site CSO | 234/1129 |  |  |  | 2 | 1 | 99.99%
Northumbrian Water | Derwent Water Terrace CSO (BT022) | EPRAB3090VG |  |  | Spittal | 6.4 | 7 | 99.99%
Northumbrian Water | Derwentside House CSO | 234/1142 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Devonshire Road (East) CSO | EPRCP3526GZ |  |  |  | 0 | 0 | 98.54%
Northumbrian Water | Devonshire Road (West) CSO | EPRCP3525XM |  |  |  | 0.25 | 1 | 99.47%
Northumbrian Water | Dinnington East SPS | 226/0102 | 226/0102-01 |  |  | 52.6067 | 10 | 100%
Northumbrian Water | Dinnington West SPS | 226/0204 | 226/0204-01 |  |  | 51.75 | 22 | 99.41%
Northumbrian Water | Dipton STW - CSO Inlet | 234/D/0005 |  |  |  | 490.58 | 88 | 99.96%
Northumbrian Water | Dipton STW - Storm Tank | 234/A/0657 |  |  |  | 587.1106 | 30 | 100% | Installed 16/11/20
Northumbrian Water | Dipwood Road CSO (G016) | 234/1126 |  |  |  | 30 | 26 | 87.39% | Traffic management required to core for antenna led to long turn around for maintenance visits. Comms. failed 20/04/20-15/05/20, 29/06/20-17/06/20.
Northumbrian Water | Dock Road CSO (BT44) | 210/1363 |  |  | Spittal | 39.7667 | 30 | 99.99%
Northumbrian Water | Don Valley SPS | Permit Anomaly |  |  |  | 91.8083 | 24 | 100%
Northumbrian Water | Donwell Primary School CSO | 235/1951 |  |  |  | 49.5 | 29 | 99.94%
Northumbrian Water | Dormer Way CSO (L071) | 254/1808 |  |  |  | 0.25 | 1 | 99.23%
Northumbrian Water | Downe Street SPS CSO | 256/1077 | 256/1077-01 |  |  | 195.25 | 27 | 99.62%
Northumbrian Water | Drysdale Crescent CSO | 226/1252 |  |  |  | 4 | 7 | 88.76% | Suffered from water ingress and connection between sensor and logger became corrupt. Therefore the logger sent no data back, but dialled in. Difficult to identify these issues, and problem is persistent. Issue between 03/04/20-28/04/20. Comms. then failed 29/10/20-05/11/20 & 11/11/20-19/11/20.
Northumbrian Water | Dudley First School CSO | 226/1257 |  |  |  | 0 | 0 | 99.72%
Northumbrian Water | Dudley Middle School CSO | 226/1259 |  |  |  | 4 | 6 | 97.38%
Northumbrian Water | Duke Street CSO | 235/1714 |  |  |  | 18.25 | 14 | 99.71%
Northumbrian Water | Dukes Walk CSO (NTY031) | 235/1982 |  |  | Whitley Bay | 0 | 0 | 100%
Northumbrian Water | Dunn Street CSO DER112 | 235/1929 |  |  |  | 5 | 5 | 99.98%
Northumbrian Water | Dunstan STW | 221/0912 | 221/0912-02 |  |  | 0 | 0 | 100% | Installed 02/12/20
Northumbrian Water | Dunston Flour Mill (West) CSO | 235/1738 |  |  |  | 306.1333 | 33 | 99.99%
Northumbrian Water | Durham City (Pelaw Wood No 1) CSO | 245/0914 |  |  |  | 97.5 | 35 | 99.64%
Northumbrian Water | Durham Road (Ref No 36) | 234/1152 |  |  |  | 0.75 | 3 | 96.35%
Northumbrian Water | Durham Road CSO | 235/1884 |  |  |  | 2 | 2 | 99.99%
Northumbrian Water | Durham Road CSO | 243/E/0569 |  |  |  | 4.25 | 10 | 99.64%
Northumbrian Water | Durham Road CSO | 245/1076 |  |  |  | 0.25 | 1 | 99.94%
Northumbrian Water | Durham Skills Centre CSO (DU008) | 244/1017 |  |  |  | 19 | 15 | 92.95%
Northumbrian Water | Durham Street CSO | 255/1155 |  |  | Seaham Hall | 1.8667 | 8 | 99.92%
Northumbrian Water | Durham University STW - CSO Inlet | 245/1064 | C |  |  | 608.8006 | 45 | 99.89%
Northumbrian Water | Durham University STW - Storm Tank | 245/1064 | B |  |  | 466.9803 | 44 | 99.89%
Northumbrian Water | Easson Road / Dodds Street CSO | EPRBB3695WG |  |  |  | 0 | 0 | 62.79% | Spurious data received from this unit from 25/06/20-10/09/20. Cello visited in that period but issue not resolved, so a Point Blue was installed on 10/09/20. Comms. fine since other than a period between 19/10/20-29/10/20.
Northumbrian Water | East Boldon CSO No 6 | 235/F/0616 |  |  |  | 57.25 | 46 | 99.56%
Northumbrian Water | East End CSO | 241/1092 |  |  |  | 65.75 | 38 | 99.72%
Northumbrian Water | East End CSO | 253/1264 |  |  |  | 55 | 42 | 97.07%
Northumbrian Water | East Farm CSO | 233/1081 |  |  |  | 2 | 4 | 99.99%
Northumbrian Water | East Ford Road SPS | 225/0939 | A |  |  | 4.1306 | 6 | 99.42%
Northumbrian Water | East Hartford SPS | 226/1089 | 226/1089-02 |  |  | 172.5 | 34 | 99.02%
Northumbrian Water | East Hendon Road CSO | EPRCB3199EC |  |  |  | 0 | 0 | 98.15%
Northumbrian Water | East Howle Howls STW | 243/1026 | 243/1026-02 |  |  | 34.0289 | 6 | 100%
Northumbrian Water | East Knitsley Grange Farm CSO | 244/0997 |  |  |  | 252.25 | 44 | 84.29% | Poor signal area. Comms. failed 26/10/20-03/11/20, 20/11/20-26/11/20, 29/11/20-end of year.
Northumbrian Water | East Sleekburn SPS | 226/1272 | 226/1272-01 |  |  | 41.25 | 17 | 99.97%
Northumbrian Water | East Street (was Swinburn Street East End) CSO | 235/1924 |  |  |  | 8.1169 | 16 | 100%
Northumbrian Water | East Tanfield STW - CSO Inlet | 235/1871 | A3 |  |  |  |  | 0% | Monitor installed but data not recovered. Investigation undertaken.
Northumbrian Water | East Tanfield STW - Storm Tank | 235/1871 | A2 |  |  | 545.7319 | 36 | 99.91% | Point upgraded from 16/11/20.
Northumbrian Water | East Terrace CSO | 255/1190 |  |  |  | 10.1 | 8 | 92.06%
Northumbrian Water | East View CSO | 245/1074 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Eastbourne East & West CSO | 254/1843 |  |  |  | 191.18/133.21 | 58/50 | 90.61%/100% | Multiple meters on tanks for a single discharge activity. Investigation into a single meter to be conducted.
Northumbrian Water | Eastbourne South/Dundas St CSO | 254/1380 |  |  |  | 216.75 | 51 | 98.74%
Northumbrian Water | Eastern Ave CSO | 235/F/0651 |  |  |  | 59.25 | 28 | 98.61%
Northumbrian Water | Eastern Way CSO | 226/A/0971 |  |  |  | 92.5 | 25 | 99.71%
Northumbrian Water | Ebchester SPS | 234/0989 | 234/0989-01 |  |  | 233.7761 | 41 | 99.95%
Northumbrian Water | Eden Walk CSO (STY034) | 235/1969 |  |  |  | 24 | 24 | 99.94%
Northumbrian Water | Edinburgh Drive CSO | 253/1076 |  |  |  | 20.75 | 8 | 98.01%
Northumbrian Water | Edmondsley STW | 245/0839 |  |  |  | 590.5494 | 56 | 100%
Northumbrian Water | Edna Street | 243/0981 |  |  |  | 111 | 38 | 99.97%
Northumbrian Water | Egglescliffe Bank CSO | 254/1179 |  |  |  | 97.5 | 76 | 99.99% | Set to 2 minutes to resolve data spikes.
Northumbrian Water | Eggleston STW CSO (TE001) | 251/0926 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Eglingham STW CSO | Permit Anomaly |  |  |  | 1.16 | 3 | 99.59% | Installed 24/04/20
Northumbrian Water | Eilansgate CSO | 233/1241 |  |  |  | 0 | 0 | 98.86%
Northumbrian Water | Eland Lane SPS | 226/A/0965 | 226/A/0965 Condition 1 (Storm Sewage) |  |  | 0 | 0 | 93.57%
Northumbrian Water | Eland Lane SPS | 226/G/0174 |  |  |  | 466.7139 | 50 | 100%
Northumbrian Water | Elder Cottages | 225/1076 |  |  |  | 12.25 | 18 | 98.77%
Northumbrian Water | Eldon Street CSO (STY067) | 235/1944 |  |  |  | 259.5 | 49 | 96.59%
Northumbrian Water | Elemore Vale SPS | 245/1399 | 245/1399-02 |  |  | 0.083056 | 3 | 100%
Northumbrian Water | Ellingham STW | 221/1056 | 221/1056-03 |  |  | 12.5 | 4 | 99.85%
Northumbrian Water | Elmwood Gardens CSO | 235/1568 |  |  |  | 71.6333 | 57 | 99.99%
Northumbrian Water | Elsdon STW | 231/1027 | A2 |  |  | 4.3464 | 6 | 95.41% | Installed 25/03/20
Northumbrian Water | Elvet Syphon CSO | NPSWQD004521 |  |  |  | 83.1 | 26 | 86.23% | Suffers from water ingress and connection between sensor and logger becomes corrupt. Therefore the logger sends no data back, but dials in. Issue from 07/09/20-27/10/20. Not rectified sooner as the chamber has an poor setup with flows covered by screens. Work had to be arranged to allow line of sight.
Northumbrian Water | Elwick SPS | 254/1076 | A1 |  |  | 2.5 | 9 | 94.5%
Northumbrian Water | Elwin Place CSO | 245/1275 |  |  |  | 21.75 | 21 | 99.64%
Northumbrian Water | Embleton Low Mill SPS | 221/0987 | 221/0987-01 |  |  | 0 | 0 | 99.96%
Northumbrian Water | Embleton STW CSO | 221/G/0336 |  |  |  | 7.1006 | 7 | 84.29% | Installed 14/04/20 Logger lost comms. during commissioning period from 31/07/20-03/09/20.
Northumbrian Water | Eppleby CSO | 252/1129 |  |  |  | 47.5 | 13 | 99.99%
Northumbrian Water | Eppleby STW | 25/02/1107 | 25/02/1107-02 |  |  | 2739.4678 | 220 | 100%
Northumbrian Water | Escomb SPS | 241/1023 | A1 |  |  | 390.5 | 43 | 99.81%
Northumbrian Water | Esh Winning CSO Point A2 | 244/E/0307 |  |  |  | 98.5 | 26 | 94.69%
Northumbrian Water | Esh Winning SPS | 244/0884 | A |  |  | 0.0033333 | 1 | 99.58%
Northumbrian Water | Esh Winning STW | 244/1026 | A2 |  |  | 340.6403 | 23 | 99.26% | Installed 06/04/20
Northumbrian Water | Eskdale Road CSO (Ref L14) | 254/1916 |  |  |  | 5.25 | 8 | 99.99%
Northumbrian Water | Essex Close CSO | 235/1319 |  |  |  | 9.7333 | 22 | 99.99%
Northumbrian Water | Etal Sewage Works | 210/0899 | B |  |  |  |  | 0% | Installed 20/03/20 in acceptance phase.
Northumbrian Water | Etherley Lane (No 100) CSO | EPRBB3997RC |  |  |  | 0 | 0 | 84.56% | Comms. failed 11/11/20-end of year. Was visited on 18/11/20 however comms. weren't restored on old unit so stock of new logger required for install.
Northumbrian Water | Etherley Lane (No 87) CSO | EPRBB3996AW |  |  |  | 0 | 0 | 95.71%
Northumbrian Water | Etherley Lane CSO | 241/1156 |  |  |  | 202.5 | 44 | 99.98%
Northumbrian Water | Evenwood Lane CSO | NPSWQD006151 |  |  |  | 31 | 17 | 91.83%
Northumbrian Water | Factory Road CSO | 233/0911 |  |  |  | 32.9 | 10 | 99.99%
Northumbrian Water | Fair View CSO (DER142) | 244/1014 |  |  |  | 127.5 | 31 | 99.85%
Northumbrian Water | Fairfield Industrial Park SPS | 235/1749 | 235/1749-01 |  |  | 0 | 0 | 97.25%
Northumbrian Water | Fairfield View CSO A013 | 223/G/0089 |  |  |  | 0 | 0 | 93.27%
Northumbrian Water | Falstone & Stannersburn STW | 231/A/0490 | [5 empty] | 0% | Unmonitored at present. Scheduled to be installed.
Northumbrian Water | Falstone & Stannersburn STW | 231/A/0491 | [5 empty] | 0% | Unmonitored at present. Scheduled to be installed.
Northumbrian Water | Farne Avenue CSO | 235/2004 |  |  |  | 2 | 6 | 97.45%
Northumbrian Water | Fatfield CSO 3 | Permit Anomaly |  |  |  | 0.25 | 1 | 94.2% | Permit anomaly to be corrected.
Northumbrian Water | Felton Recreation Ground CSO | 223/1004 |  |  |  | 37.25 | 32 | 99.63%
Northumbrian Water | Felton STWs - CSO Inlet | 223/0993 | 223/0993-03 |  |  | 15.7092 | 31 | 100%
Northumbrian Water | Felton STWs - Storm Tank | 223/0993 | 223/0993-02 |  |  | 1300.3511 | 94 | 40.87% | Installed pre-2020 but not operable until 4/8/20 hence low operability.
Northumbrian Water | Fenwick (Berwick) STW | 221/0968 | 221/0968-02 |  |  | 35.7917 | 8 | 100% | Installed 07/09/20
Northumbrian Water | Ferguson Motor Repairs CSO | EPRYB3435AJ |  |  |  | 0 | 0 | 96.31% | Installed 21/12/20
Northumbrian Water | Fern Drive CSO | 226/G/0058 | [5 empty] | 0% | Monitor installed but not commissioned. Investigation to address the matter required. Highlighted on the change control form.
Northumbrian Water | Fern Drive CSO | NPSWQD006838 |  |  |  | 12.25 | 8 | 99.98%
Northumbrian Water | Fernie Road (31) CSO | QR.25/06/0976 |  |  |  | 30.5 | 10 | 99.99%
Northumbrian Water | Ferryboat Lane SPS | 245/1208 | 245/1208-01 |  |  | 65.75 | 8 | 93.42%
Northumbrian Water | Ferryhill North SPS | 243/0978 | A1 |  |  | 44.5 | 35 | 99.95%
Northumbrian Water | Ferryhill SPS | 253/1037 | A |  |  | 38.955 | 19 | 99.99%
Northumbrian Water | Fieldon Bridge CSO | 242/1041 |  |  |  | 750.5 | 84 | 99.58%
Northumbrian Water | Fifth Row CSO | 224/0984 |  |  |  | 3.5 | 2 | 82.44% | In a poor comms. area. Due to a technical problem with Cello daily comms. were being received but no sewer level data were being sent. Difficult to identify this issue quickly, but raised on 04/09/20. Period without data started on 31/08/20. Contractor did not attend until 03/11/20. Comms. ok since.
Northumbrian Water | Finchale View CSO | 245/1294 |  |  |  | 77.5 | 43 | 99.04%
Northumbrian Water | Finings Avenue SPS | 244/A/0528 | 244/A/0528-01 |  |  | 49.7686 | 23 | 100%
Northumbrian Water | Fir Tree STW | 241/1013 | B |  |  | 485.205 | 30 | 99.97% | Point upgraded from 04/12/20.
Northumbrian Water | First Row CSO | 224/0969 |  |  |  | 2.25 | 7 | 99.97%
Northumbrian Water | First School CSO NTY002 | 226/G/0173 |  |  |  | 179.5 | 43 | 99.98%
Northumbrian Water | Fish Quay CSO | 235/1914 |  |  |  | 53.6942 | 17 | 100%
Northumbrian Water | Fishburn Bridge CSO | NPSWQD008199 |  |  |  | 32.5 | 35 | 99.52%
Northumbrian Water | Fishburn STW - CSO Inlet | 25/03/1234 | 25/03/1234-03 |  |  | 29.0564 | 11 | 100%
Northumbrian Water | Fishburn STW - Storm Tank | 25/03/1234 | 25/03/1234-02 |  |  | 9.6347 | 2 | 100% | Installed 15/12/20
Northumbrian Water | Floaters Mill SPS CSO | 245/E/0594 | 245/E/0594-01 |  |  | 0.10444 | 5 | 100%
Northumbrian Water | Forster St / Easson Road CSO | EPRBB3791RD |  |  |  | 0 | 0 | 91.21%
Northumbrian Water | Foundry Lane No 3 CSO | 235/1947 |  |  |  | 54.3 | 32 | 99.12%
Northumbrian Water | Foundry Lane No1 CSO | 235/1528 |  |  |  | 59.4667 | 37 | 99.99%
Northumbrian Water | Fourstones STW - Storm Tank | 232/1119 | 232/1119-03 |  |  | 8.9561 | 1 | 72.43% | Installed 07/09/20. Logger failed 01/12/20. Maintenance request raised 11/02/21.
Northumbrian Water | Frankland Lane CSO | 245/1272 |  |  |  | 197 | 35 | 98.72%
Northumbrian Water | Front Street (Town Hall) CSO | 232/1168 |  |  |  | 16.75 | 17 | 99.44%
Northumbrian Water | Front Street CSO | 226/1180 |  |  |  | 28.75 | 24 | 89.66% | Comms. failed 01/09/20-08/10/20. Was visited on 18/09/20 but visit didn't restore comms. Comms. working since last visit.
Northumbrian Water | Front Street CSO | 244/0927 |  |  |  | 35.5667 | 113 | 99.99% | Set to 2 minutes to resolve data spikes. Very poor data site. Most discharges are very short duration, and believe a lot aren't real discharges, but data are very poor it is difficult to analyse.
Northumbrian Water | Front Street CSO | 244/0926 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Front Street CSO | EPRJB3292WB |  |  |  | 226.5 | 67 | 99.95%
Northumbrian Water | Front Street CSO (CH68) | 245/1315 |  |  |  | 0.25 | 1 | 99.99%
Northumbrian Water | Frosterley (Willow Green) STW | 241/1104 | 241/1104-03 |  |  | 1117.92 | 88 | 100%
Northumbrian Water | Furness SPS | QR.25/04/1543 | S1 |  |  | 0 | 0 | 100%
Northumbrian Water | Gainford STW - CSO Inlet | 25/02/1078 | 25/02/1078-04 |  |  | 75.25 | 15 | 93.66%
Northumbrian Water | Gainford STW - Storm Tank | 25/02/1078 | 25/02/1078-03 |  |  | 857.7825 | 69 | 99.88%
Northumbrian Water | Galgate CSO | 252/1122 |  |  |  | 16.25 | 13 | 99.99%
Northumbrian Water | Gardner Avenue | 243/1025 |  |  |  | 2.5 | 4 | 97.22%
Northumbrian Water | Gas Lane CSO | 235/1740 |  |  |  | 0 | 0 | 98.5% | Changed to 2 minute logging 05/03/20.
Northumbrian Water | Gellesfield CSO | 234/1059 |  |  |  | 119 | 45 | 95.49%
Northumbrian Water | Gill Cemetery CSO (SU061) - M2 Monitoring Point | 245/1371 | A1 |  |  | 161.25 | 59 | 99%
Northumbrian Water | Gill Cemetery CSO (SU061) - M3 Monitoring Point | 245/1371 | A1 |  |  | 0.755 | 4 | 99.98%
Northumbrian Water | Gillas Lane East CSO (SU32) | 245/1360 |  |  |  | 0.25 | 1 | 99.97%
Northumbrian Water | Gillas Lane West CSO (SU30) | 245/1359 |  |  |  | 31.25 | 26 | 99.97%
Northumbrian Water | Gladstone Street (G1) | 253/A/0942 |  |  |  | 4 | 10 | 93.8%
Northumbrian Water | Glasshouse Street SPS | 235/1767 | 235/1767-01 |  |  | 474.5 | 122 | 99.27%
Northumbrian Water | Glaxo West CSO | 225/1025 |  |  |  | 49.25 | 34 | 99.95%
Northumbrian Water | Glebe Estate CSO | 255/1124 |  |  |  | 0.5 | 2 | 96.55%
Northumbrian Water | Glendale Avenue Relief Sewer | 235/1952 |  |  |  | 34.25 | 18 | 99.98%
Northumbrian Water | Glentower Grove CSO | 255/5046 |  |  | Seaton Carew (North) | 11.2917 | 1 | 99.9%
Northumbrian Water | Goatbeck Terrace CSO | 244/0947 |  |  |  | 0.75 | 3 | 99.99%
Northumbrian Water | Golden Lion Pump CSO & SPS | 245/1169 | 245/1169-01 |  |  | 97.5375 | 27 | 99.99%
Northumbrian Water | Golf Course Road CSO | 245/1369 |  |  |  | 0.25 | 1 | 99.97%
Northumbrian Water | Gomer Terrace CSO | 241/1056 |  |  |  | 17.25 | 7 | 87.17% | Comms. failed 16/11/20-end of year. Was visited on 24/11/20 however comms. weren't restored on old unit so stock of new logger required for install.
Northumbrian Water | Grange Bank CSO (WV112) | 241/1141 |  |  |  | 34.5 | 13 | 99.98%
Northumbrian Water | Grange Mill CSO | Permit Anomaly |  |  |  | 22.5 | 14 | 99.96% | Permit anomaly to be corrected.
Northumbrian Water | Grange Park CSO (WK016) | 226/1265 |  |  |  | 458.25 | 77 | 99.99%
Northumbrian Water | Grange Road CSO A004 | 223/G/0088 |  |  |  | 0.5 | 2 | 99.99%
Northumbrian Water | Grange Villa CSO | 245/1214 |  |  |  | 0 | 0 | 99.95%
Northumbrian Water | Grangefield Road CSO | 25/04/1627 |  |  |  | 22.25 | 11 | 97.42%
Northumbrian Water | Granville Terrace CSO | 256/1068 |  |  | Redcar Sands - Granville Terrace | 157.0333 | 33 | 99.92%
Northumbrian Water | Grassbanks CSO | 235/A/0510 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Grassholm Place CSO | 235/1896 |  |  |  | 227 | 40 | 99.28%
Northumbrian Water | Gray Lane CSO | 252/1053 |  |  |  | 49 | 28 | 92.99%
Northumbrian Water | Gray's Road CSO | 25/04/1661 |  |  |  | 9.75 | 9 | 99.97%
Northumbrian Water | Grays Road CSO (ST29) | 25/04/1628 |  |  |  | 778.75 | 72 | 99.91%
Northumbrian Water | Graythorp STW | 25/04/1758 | 25/04/1758-02 |  |  | 1772.3875 | 169 | 99.99%
Northumbrian Water | Great Ayton STW | 25/04/1859 | A2 |  |  | 741.595 | 62 | 99.96% | Point upgraded from 11/11/20.
Northumbrian Water | Great Broughton & Kirby CSO MH 6 | 254/E/0277 |  |  |  | 14.5 | 13 | 99.91%
Northumbrian Water | Great Broughton STW | 25/04/1676 | 25/04/1676-03 |  |  | 2215.2114 | 119 | 100%
Northumbrian Water | Greatham STW - CSO Inlet | 25/04/1858 | 25/04/1858-05 |  |  |  |  | 0% | Unmonitored at present. Scheduled to be installed.
Northumbrian Water | Greatham STW - Storm Tank | 25/04/1858 | 25/04/1858-04 |  |  | 458.5728 | 70 | 99.98%
Northumbrian Water | Green Bridge CSO (DER 137) | 234/1110 |  |  |  | 59.4389 | 15 | 99.99%
Northumbrian Water | Green Cresent CSO | 226/1255 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Green Lane CSO | 225/1069 |  |  |  | 63.25 | 20 | 99.49%
Northumbrian Water | Greenford Road C18-102 | Permit Anomaly |  |  |  | 0.5 | 2 | 97.72% | Permit anomaly to be corrected.
Northumbrian Water | Greenhead SPS | 232/0987 | 232/0987-01 |  |  | 463.2042 | 52 | 99.99%
Northumbrian Water | Green's Lane CSO (ST015) | 254/E/0361 |  |  |  | 5.25 | 7 | 98.98%
Northumbrian Water | Greenside CSO Lead Road | EPRBB3791AL |  |  |  | 0 | 0 | 98.09%
Northumbrian Water | Gribdale STW | 256/1062 | 256/1062-03 |  |  | 4.25 | 3 | 97.37%
Northumbrian Water | Grinkle Road CSO | 254/1912 |  |  |  | 3.25 | 2 | 99.99%
Northumbrian Water | Grove Road CSO (M009) | 254/1851 |  |  |  | 40.5 | 19 | 99.75%
Northumbrian Water | Grove Terrace CSO (DU005) | 244/1007 |  |  |  | 48.75 | 40 | 99.99%
Northumbrian Water | Guisborough Storm Works | 25/06/1021 | 25/06/1021-02 |  | Saltburn Pier | 151.6889 | 22 | 100%
Northumbrian Water | Gunnergate Lane CSO | 25/04/1666 |  |  |  | 0 | 0 | 97.78%
Northumbrian Water | Gunnerton STW - 3-6xDWF | 231/1078 | 231/1078-03 |  |  |  |  | 0% | The EDM Tracker only identified one output and monitoring has been provided for this. This second activity is unmonitored at present and scheduled to be installed.
Northumbrian Water | Gunnerton STW - 6xDWF | 231/1078 | 231/1078-04 |  |  | 13.7211 | 2 | 34.97% | Installed 15/04/20. Logger lost comms. a number of times during commissioning period for short intervals. They then failed from 05/07/20-18/12/20. Monitoring uncertainty - Data is for the 6xDWF. An additional monitor is required for schedule 231/1078-03 on the consent which wasn't listed on the EDM Tracker.
Northumbrian Water | Hadston SPS - The Lady Burn | 224/0990 | 224/0990-01 - Consent Point 2 |  |  | 265.9258 | 33 | 100%
Northumbrian Water | Hadston SPS - The North Sea | 224/0990 | 224/0990-01 - Consent Point 1 |  |  | 1339.0008 | 80 | 100%
Northumbrian Water | Haggerston Castle STW | 210/A/0849 | 210/A/0849-02 |  |  | 659.8056 | 35 | 97.22% | Point changed to logger from install on 23/10/20.
Northumbrian Water | Hall Farm CSO (SE037) | 243/0993 |  |  |  | 4.5 | 10 | 99.96%
Northumbrian Water | Hall Lodge CSO | 221/1003 |  |  |  | 42.5 | 19 | 99.97%
Northumbrian Water | Halton Lea Gate CSO | 232/G/0063 |  |  |  | 79.25 | 32 | 99.76%
Northumbrian Water | Haltwhistle STW - CSO Inlet | 232/1098 | 232/1098-03 |  |  | 281.9889 | 82 | 100%
Northumbrian Water | Haltwhistle STW - Storm Tank | 232/1098 | 232/1098-04 |  |  | 439.1617 | 43 | 100%
Northumbrian Water | Hamilton Row | 244/E/0308 |  |  |  | 105.75 | 34 | 99.8%
Northumbrian Water | Hamsterley Colliery SPS | 234/F/0368 | 234/F/0368 (Storm Sewage) |  |  | 170 | 37 | 94.26%
Northumbrian Water | Hamsterley CSO | 241/C/0419 |  |  |  | 0.5 | 2 | 93.02%
Northumbrian Water | Hamsterley Mill CSO | 234/1084 |  |  |  | 137.25 | 42 | 99.68%
Northumbrian Water | Hamsterley STW | 241/1147 | 241/1147-02 |  |  | 63.5175 | 16 | 99.8% | Installed 16/04/20
Northumbrian Water | Harbottle STW | 223/0990 | 223/0990-02 |  |  | 177.8425 | 61 | 99.88%
Northumbrian Water | Harbour SPS | 221/0914 | 221/0914-A (Storm Sewage) |  | Seahouses North | 9.8242 | 10 | 99.93%
Northumbrian Water | Harrowgate Hill SPS & CSO | 253/1276 | 253/1276-01 |  |  | 10.8292 | 12 | 100%
Northumbrian Water | Hartford Bridge SPS | 226/1248 | 226/1248-01 |  |  | 0 | 0 | 100%
Northumbrian Water | Hartley Caravan Park SPS | 226/1090 | 226/1090-02 |  |  | 3.5683 | 12 | 99.93%
Northumbrian Water | Harton Low Staithes CSO | 235/1908 |  |  |  | 160.3311 | 33 | 100%
Northumbrian Water | Harton Mill Dam CSO | 235/1907 |  |  |  | 5.25 | 5 | 98.94%
Northumbrian Water | Harwal Road CSO (Ref.L16) | 25/04/1782 |  |  |  | 49.25 | 22 | 99.45%
Northumbrian Water | Haswell CSO No 18 | 255/E/0643 |  |  |  | 23.5 | 13 | 99.97%
Northumbrian Water | Haugh Lane CSO | 233/1224 | [5 empty] | 0% | Unmonitored at present. Scheduled to be installed.
Northumbrian Water | Hawthorn CSO | 255/E/0640 |  |  |  | 44.5 | 34 | 92.14%
Northumbrian Water | Hawthorne Close CSO | 255/1180 |  |  |  | 8 | 7 | 99.99%
Northumbrian Water | Hay Street CSO (SU056) | 245/1374 |  |  |  | 15.25 | 23 | 99.86%
Northumbrian Water | Haydon Bridge STW | 232/1165 | 232/1165-02 |  |  | 78.6775 | 23 | 98.94% | Point upgraded from 26/11/20.
Northumbrian Water | Headlam SPS | 252/1002 | A |  |  | 0.026944 | 1 | 99.98% | Point changed to logger from install on 12/12/20.
Northumbrian Water | Heaton CSO | EPRCB3192VE |  |  |  | 6.5 | 5 | 74.59% | Sensor installed on 08/11/20 and poor data has been received since, reducing operability. Contractor required to reattend to resolve issues.
Northumbrian Water | Heaton Gardens SPS | 235/1388 | A |  |  |  |  | 0% | Unmonitored at present. Scheduled to be installed.
Northumbrian Water | Heddon Banks Farm CSO | 233/1237 |  |  |  | 13.5 | 21 | 99.98%
Northumbrian Water | Heddon-On-The-Wall STW | 233/1266 | 233/1266-02 |  |  | 30.7986 | 36 | 99.92%
Northumbrian Water | Heighington CSO | 25/03/1240 |  |  |  | 19.5 | 13 | 99.57%
Northumbrian Water | Hendon STW | 245/1213 | 245/1213-01 |  |  |  |  | 0% | Monitor present. Data for 2019 under review between EA and NWL. Agreed monitoring data will follow in the bespoke annual return.
Northumbrian Water | Hepple STW | 223/0995 | 223/0995-02 |  |  |  |  | 0% | Installed 04/03/20 in acceptance phase.
Northumbrian Water | Hepscott STW | 226/1281 | A2 |  |  |  |  | 0% | Storm tank completion date 01/04/2021.
Northumbrian Water | Herrington CSO West Park East (New) | 245/1301 |  |  |  | 3 | 5 | 99.99% | Data provided for additional site not identified on the EDM Tracker as requested by REDACTED letter dated 08/02/21.
Northumbrian Water | Hetton Le Hole Day Centre CSO | 245/1365 |  |  |  | 7.75 | 7 | 99.99%
Northumbrian Water | Hetton Park Bowling Green CSO | 245/1364 |  |  |  | 22.75 | 17 | 99.15%
Northumbrian Water | Hetton Park CSO (SU34) | 245/1362 |  |  |  | 11.75 | 9 | 96.61%
Northumbrian Water | Hetton Road CSO (SU33) | 245/1361 |  |  |  | 39.5 | 18 | 62.62% | REDACTED TEXT. Also technical issue with Cello previously installed in here dialling in and causing telemetry issues. Comms. failed 13/05/20-15/06/20, 05/07/20-07/07/20, 28/07/20-28/08/20, 28/09/20-21/10/20, 27/11/20-end of year. Now resolved.
Northumbrian Water | Hexham (The Larches) SPS | 233/1042 | 233/1042-01 |  |  | 22.8825 | 18 | 99.98%
Northumbrian Water | Hexham CSO | EPRBB3598RX |  |  |  | 0.5 | 1 | 12.67% | Monitor installed 09/09/20 and has experienced poor comms. since.
Northumbrian Water | Hexham STW | 233/1281 | 233/1281-02 |  |  | 773.5872 | 98 | 100%
Northumbrian Water | High Carr Road CSO | 245/1300 |  |  |  | 224.25 | 84 | 99.95%
Northumbrian Water | High Friarside CSO | 234/A/0590 |  |  |  | 75.25 | 21 | 99.99%
Northumbrian Water | High Hauxley SPS | 224/0947 | 224/0947-01 |  |  | 36.5472 | 12 | 99.96%
Northumbrian Water | High Relief Overflow | 255/1158 |  |  |  | 0 | 0 | 94.06% | Installed 21/12/20. Logger not yet commissioned hence unvalidated data and due to communication issues low operability.
Northumbrian Water | High Spen CSO (Rowlands Gill 12) | EPRBB3897RH |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | High Spen CSO (Rowlands Gill 6) | EPRBB3897WE |  |  |  | 0 | 0 | 99.98%
Northumbrian Water | High Spen SPS | 233/1162 | 233/1162-01 |  |  | 147.6467 | 53 | 99.71% | Point changed to logger from install on 27/10/20.
Northumbrian Water | High Street CSO | 245/1155 |  |  |  | 4.25 | 7 | 99.99%
Northumbrian Water | High Street CSO | EPRCB3190WC |  |  |  | 0 | 0 | 97.87%
Northumbrian Water | High Street West CSO (G066) | 235/1927 |  |  |  | 90.8667 | 58 | 99.99%
Northumbrian Water | High Waterhouses Farm CSO (DU78) | 244/1018 |  |  |  | 162.75 | 33 | 99.95%
Northumbrian Water | Hills Joinery CSO | 254/0047 |  |  |  | 424.1983 | 48 | 100% | Point changed to logger from install on 24/11/20.
Northumbrian Water | Hilton SPS | 254/1963 | 254/1963-01 |  |  | 31.0503 | 12 | 99.97%
Northumbrian Water | Hobdale House CSO (L38) | 256/1074 |  |  |  | 5 | 7 | 99.95%
Northumbrian Water | Hollinside Sewage Disposal Works | 244/C/0282 | [5 empty] | 0% | Unmonitored at present. Scheduled to be installed.
Northumbrian Water | Hollyhill Gardens East CSO | 245/1075 |  |  |  | 225.5 | 67 | 99.62%
Northumbrian Water | Holmhill Field CSO | NPSWQD009250 |  |  |  | 55.5 | 32 | 91.1%
Northumbrian Water | Holy Island STW | 221/1016 | 221/1016-03 |  |  | 73.1347 | 16 | 100%
Northumbrian Water | Holywell House (West of) CSO | 226/1186 |  |  |  | 6 | 1 | 99.7%
Northumbrian Water | Holywell SPS | 226/0947 | A |  |  | 7.0114 | 2 | 100%
Northumbrian Water | Hopgarth Gardens CSO | 245/1268 |  |  |  | 20.5 | 16 | 98.29%
Northumbrian Water | Horden Dene SPS | 255/1146 | 255/1146-01 |  |  | 334.2881 | 59 | 100% | Point upgraded from 26/11/20.
Northumbrian Water | Horden STW | 255/1145 | 255/1145-03 |  |  | 1.25 | 2 | 99.93%
Northumbrian Water | Horncliffe North (No 1) STW | 210/0887 | 210/0887-02 |  |  | 0.25 | 1 | 99.99% | Multiple meters on tanks for a single discharge activity . Discussion with EA regarding potential permit change.
Northumbrian Water | Horncliffe North (No 2) STW | 210/0887 | 210/0887-02 |  |  | 42.5647 | 23 | 55.01% | Installed 03/09/20. Four periods since install where data not recorded for approximately a day. This reduces operability drastically as unit only installed late in the year. Additionally, unit in alarm for a few periods where visual checks have confirmed the site isn't discharging so logger marked inoperable for these periods. Multiple meters on tanks for a single discharge activity . Discussion with EA regarding potential permit change.
Northumbrian Water | Houghton Le Spring CSO | EPRBB3899VA |  |  |  | 57.75 | 39 | 98.67%
Northumbrian Water | Houghwell House CSO | 235/1711 |  |  |  | 38.75 | 26 | 99.74%
Northumbrian Water | Howden Road CSO (NTY 040) | 235/1899 |  |  |  | 6.25 | 5 | 99.97%
Northumbrian Water | Howden Wood CSO No 46 | 234/F/0400 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Howdon (Adj A19 Roundabout) CSO | NPSWQD009134 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Howdon STW - CSO Inlet | 235/1804 | 235/1804-01 |  |  | 8.5667 | 9 | 100%
Northumbrian Water | Howdon STW - CSO Inlet - North Bank | 235/1695 | 235/1695-03 |  |  | 460.6653 | 55 | 100%
Northumbrian Water | Howdon STW - CSO Inlet - South Bank | 235/1695 | 235/1695-05 |  |  | 1027.5864 | 124 | 100%
Northumbrian Water | Howdon STW - Primary Treated Storm | 235/1695 | 235/1695-07 |  |  | 2498.1278 | 183 | 100%
Northumbrian Water | Howling Lane CSO (A046) | 222/0861 |  |  |  | 53.5 | 45 | 99.43%
Northumbrian Water | Hughbourne Street CSO | Permit Anomaly |  |  |  | 0 | 0 | 99.99% | Permit anomaly to be corrected.
Northumbrian Water | Humshaugh STW | 231/1108 | 231/1108-02 |  |  | 175.0119 | 20 | 99.77% | Point upgraded from 26/11/20.
Northumbrian Water | Huntshield Ford CSO (WV097) | 241/1157 |  |  |  | 271 | 44 | 99.32%
Northumbrian Water | Hunwick Lane CSO (WV70) | 243/0994 |  |  |  | 0.5 | 1 | 99.99%
Northumbrian Water | Hurworth Place SPS | 254/1019 | A1 |  |  | 9.3689 | 14 | 100%
Northumbrian Water | Hustledown Road CSO | 245/1257 |  |  |  | 23.75 | 24 | 99.94%
Northumbrian Water | Hustledown STW | 245/1247 | A2 |  |  | 1094.2967 | 69 | 100% | Point upgraded from 25/11/20.
Northumbrian Water | Hutton Rudby SPS CSO & EO | 25/04/1643 | A1 |  |  | 271.2503 | 51 | 99.92%
Northumbrian Water | Hutton Rudby STW | 25/04/1751 | 25/04/1751-02 |  |  | 87.3511 | 16 | 100%
Northumbrian Water | Ingleby Greenhow STW | 25/04/1740 | 25/04/1740-03 |  |  | 2207.6683 | 116 | 99.99% | Point upgraded from 25/11/20.
Northumbrian Water | Inlet CSO (12 x DWF) | 231/A/0454 | [5 empty] | 0% | Unmonitored in 2020. Monitoring point confirmed 05/02/2021.
Northumbrian Water | Inlet CSO (6-12 X DWF) | 231/A/0453 |  |  |  | 126.6931 | 73 | 100%
Northumbrian Water | Inlet CSO Bowsden STW | 210/1292 |  |  |  | 125.1017 | 36 | 100%
Northumbrian Water | Institute Terrace CSO | Permit Anomaly |  |  |  | 1.5 | 3 | 99.97% | Permit anomaly to be corrected.
Northumbrian Water | International Paints SPS | 235/1751 | 235/1751-01 |  |  | 86.115 | 45 | 99.98%
Northumbrian Water | Iveston Lane CSO | 244/0918 |  |  |  | 0 | 0 | 93.61%
Northumbrian Water | Jackson Avenue CSO | NPSWQD010337 |  |  |  | 307.5 | 55 | 99.99%
Northumbrian Water | James Street CSO | 25/04/1768 |  |  |  | 12 | 7 | 99.73%
Northumbrian Water | Jarrow CSO Blackett Street [D11 /101] STY057 | 235/1181 |  |  |  | 28.5 | 18 | 87.37% | Data provided for additional site not identified on the EDM Tracker as requested by REDACTED letter dated 08/02/21. Comms. failed 21/01/20. Crew attended on 07/02/20 but contractor had scheduled a 2 man crew when 4 were needed. Not reattended until 06/03/20 when comms. were restored.
Northumbrian Water | Jarrow Slake Screw SPS | 235/1405 | A |  |  | 606.7278 | 48 | 100%
Northumbrian Water | JF Kennedy Estate CSO | 245/1302 |  |  |  | 0.23333 | 1 | 99.99%
Northumbrian Water | John Street CSO | 226/1058 |  |  |  | 1038.75 | 114 | 98.81%
Northumbrian Water | Jolly Fisherman CSO | NPSWQD009505 |  |  |  | 0 | 0 | 8.748% | Operability <90% due to poor comms. - The monitor requires a site visit to download the data as it's situated in a remote location with poor network coverage and no electricity supply.
Northumbrian Water | Jubilee Place CSO | 245/1299 |  |  |  | 0.5 | 2 | 99.99%
Northumbrian Water | Jubilee Road CSO | QC.25/03/1109 |  |  |  | 40 | 23 | 99.99%
Northumbrian Water | Junction Church Rd / Dock Rd CSO | 210/1346 |  |  | Spittal | 0 | 0 | 99.99%
Northumbrian Water | Junction Damside and Staithes Lane | 225/1072 |  |  |  | 119.5 | 37 | 88.28% | Suffered from water ingress and connection between sensor and logger became corrupt. Therefore the logger sent no data back, but dialled in. Difficult to identify these issues, and problem is persistent. Issue between 03/11/20-14/12/20. Short periods of inoperability earlier in the year.
Northumbrian Water | Junction of Clavering Rd & Ruskin Rd G037 | 234/1144 |  |  |  | 2.75 | 9 | 90.52% | Data provided for additional site not identified on the EDM Tracker as requested by REDACTED letter dated 08/02/21.
Northumbrian Water | Junction of Clavering Road and Swalwel Bank CSO | 234/1143 |  |  |  | 1.1667 | 7 | 99.85%
Northumbrian Water | Junction of Hexham Road & Longrigg Roundabout CSO | 234/1159 |  |  |  | 188.2667 | 65 | 99.99%
Northumbrian Water | Kellgate Bridge CSO | QR.25/04/1573 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Kelloe STW | 243/0965 | 243/0965-03 |  |  | 232.3678 | 43 | 100%
Northumbrian Water | Kenton Rd/Rokeby Drive CSO | 235/1549 | [5 empty] | 0% | Unmonitored at present. Highlighted on the change control form.
Northumbrian Water | Kier Hardy Way CSO (SU057) | 245/1373 |  |  |  | 5 | 12 | 94.75%
Northumbrian Water | Kilburn Road CSO (ST019) | 254/D/0407 |  |  |  | 10.25 | 9 | 99.98%
Northumbrian Water | Killingworth Wagonway CSO | 235/1842 |  |  |  | 35.75 | 25 | 96.39%
Northumbrian Water | Kilton Mill CSO | 256/C/0408 |  |  |  | 0 | 0 | 95.55% | Installed 21/12/20
Northumbrian Water | Kimblesworth CSO | EPRBB3398RS | [5 empty] | 0% | Unmonitored at present. Highlighted on the change control form.
Northumbrian Water | King Oswy Drive CSO | 255/1117 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | King Street SPS | 221/1074 | 221/1074-01 |  |  | 7.6847 | 8 | 100%
Northumbrian Water | Kings Arms Lane CSO | 232/1152 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Kingsmere SPS | 235/1886 | 235/1886-01 |  |  | 0 | 0 | 99.13%
Northumbrian Water | Kingsway/Princess Street CSO | 235/1873 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Kirk Street CSO (ST005) | 254/1834 |  |  |  | 0 | 0 | 96.9%
Northumbrian Water | Kirkby SPS | 25/04/1636 | 25/04/1636-03 |  |  | 0 | 0 | 98.96%
Northumbrian Water | Kirklevington STW | 25/04/1773 | 25/04/1773-02 |  |  | 297.5708 | 35 | 99.21% | Point changed to logger from install on 14/10/20.
Northumbrian Water | Klondyke CSO | 226/1182 |  |  |  | 47.5 | 24 | 99.94%
Northumbrian Water | Knitsley Sewage Disposal Works | 244/1028 | 244/1028-02 |  |  | 145.4161 | 19 | 100% | Installed 02/10/20
Northumbrian Water | Kyloe View CSO | 210/0995 |  |  |  | 17.25 | 18 | 99.98%
Northumbrian Water | La Hacienda CSO | 233/1265 |  |  |  | 17.1667 | 12 | 92.91%
Northumbrian Water | Lackenby And South Lackenby CSO | 256/E/0259 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Lakes CSO | 256/1066 |  |  | Redcar Coatham | 3.3233 | 1 | 100%
Northumbrian Water | Lamesley CSO | 235/D/0266 |  |  |  | 54 | 13 | 96.39%
Northumbrian Water | Lamesley SPS CSO | 235/A/0837 | [5 empty] | 0% | Unmonitored at present. Scheduled to be installed.
Northumbrian Water | Lamport Street CSO | 235/1051 |  |  |  | 2 | 4 | 97.95%
Northumbrian Water | Lanchester Avenue CSO | 235/1956 |  |  |  | 16 | 9 | 99.81%
Northumbrian Water | Lanchester STW | 244/0986 | 244/0986-03 |  |  | 1016.0894 | 82 | 100% | Point upgraded from 26/11/20.
Northumbrian Water | Lands Farm CSO | 242/1028 |  |  |  | 14.5 | 12 | 99.93%
Northumbrian Water | Lanehead SPS | 223/0840 | A |  |  | 356.0992 | 36 | 99.99%
Northumbrian Water | Lanehead STW | 231/0922 | 231/0922-02 |  |  |  |  | 0% | Unmonitored at present. Scheduled to be installed.
Northumbrian Water | Langley Beck CSO | 25/03/1251 |  |  |  | 91.25 | 39 | 99.24%
Northumbrian Water | Langton Beck SPS | 252/1001 | 252/1001-A (Storm Sewage) |  |  | 191.4933 | 49 | 99.98%
Northumbrian Water | Lansbury Drive CSO | 235/1885 |  |  |  | 20.75 | 19 | 99.7%
Northumbrian Water | Lanytys Lonnen CSO | 232/0999 |  |  |  | 0.25 | 1 | 93.19%
Northumbrian Water | Laurel Avenue CSO | 245/1261 |  |  |  | 59 | 37 | 99.57%
Northumbrian Water | Layland Bridge CSO | 256/1072 |  |  | Saltburn Pier | 1.0667 | 1 | 99.94%
Northumbrian Water | Layland Bridge SPS | 256/1073 | 256/1073-01 |  | Saltburn Pier | 93.0094 | 35 | 99.96%
Northumbrian Water | Lealholme Grove CSO | 254/1931 |  |  |  | 4.5 | 8 | 99.99%
Northumbrian Water | Leamside CSO | 245/1295 |  |  |  | 9.5 | 5 | 99.98%
Northumbrian Water | Leamside STW | 245/1271 | 245/1271-03 |  |  | 1675.0642 | 101 | 99.97% | Point changed to logger from install on 18/11/20.
Northumbrian Water | Leasingthorne Farm CSO | 25/03/1252 |  |  |  | 30.75 | 36 | 98.47%
Northumbrian Water | Leasingthorne SPS CSO | 25/03/1268 | 25/03/1268-01 |  |  | 73.25 | 32 | 96.23%
Northumbrian Water | Lesbury CSO | 222/G/0185 |  |  |  | 0 | 0 | 82.38% | Technical issues with converting to Point Blue unit from 24/06/20-26/08/20.
Northumbrian Water | Levenside/Manor Close CSO | QR.25/04/1571 |  |  |  | 143.5 | 29 | 99.98%
Northumbrian Water | Lime Street/Cut Bank (2) | 235/1957 |  |  |  | 158.1 | 59 | 98.48%
Northumbrian Water | Limekiln Gill SPS | 255/1114 | A |  | Crimdon | 0.060833 | 1 | 100% | Installed 20/04/20
Northumbrian Water | Lindom Avenue CSO | 245/1379 |  |  |  | 306.4931 | 31 | 100%
Northumbrian Water | Links Road CSO | 226/1075 |  |  | Blyth South Beach | 0 | 0 | 100% | Installed 18/12/20
Northumbrian Water | Links Road CSO | Permit Anomaly |  |  | Seaton Sluice | 1.2667 | 9 | 77.32% | Suffers from intermittent comms. outages. Failed 11/06/20-22/06/20, 21/10/20-end of year. Permit anomaly to be corrected.
Northumbrian Water | Linton SPS | 224/0958 | 224/0958-02 |  |  | 0 | 0 | 100%
Northumbrian Water | Lintz Terrace CSO | 235/1708 |  |  |  | 7 | 7 | 99.97%
Northumbrian Water | Liverton Railway SPS & CSO | 256/C/0407 | 256/C/0407-A1 |  |  | 35.25 | 9 | 99.97%
Northumbrian Water | Local Avenue CSO | 245/1203 |  |  |  | 12.75 | 13 | 97.85%
Northumbrian Water | Locke Park CSO | 254/1911 |  |  |  | 4.25 | 1 | 99.99%
Northumbrian Water | Lockhaugh Road CSO | 234/A/1025 |  |  |  | 2.75 | 4 | 99.57%
Northumbrian Water | Lockhaugh Sewage Disposal Works - CSO Inlet | 234/1072 | 234/1072-04 |  |  | 15.2675 | 12 | 99.91%
Northumbrian Water | Lockhaugh Sewage Disposal Works - Storm Tank | 234/1072 | 234/1072-03 |  |  | 2166.0006 | 141 | 99.91%
Northumbrian Water | Londonderry Road/Green Lane | Permit Anomaly |  |  |  | 16.5 | 10 | 99.71% | Permit anomaly to be corrected.
Northumbrian Water | Long Bridge CSO (R005) | QC.25/02/1070 |  |  |  | 25.75 | 9 | 98.74%
Northumbrian Water | Longbeck CSO | 25/06/1018 |  |  | Marske | 16.9 | 19 | 98.61%
Northumbrian Water | Longbyre STW | 232/1155 | 232/1155-03 |  |  | 0 | 0 | 11.98% | Installed 23/04/20. Logger lost comms. during commissioning period from 15/05/20-18/12/20.
Northumbrian Water | Longhirst STW | 225/A/0861 |  |  |  | 89.4347 | 11 | 99.9% | Point changed to logger from install on 16/12/20.
Northumbrian Water | Longhorsley STW | 223/0633 | A2 |  |  | 12.6361 | 6 | 100% | Point upgraded from 04/12/20.
Northumbrian Water | Longnewton CSO (STO07) | NPSWQD009184 |  |  |  | 80.5 | 46 | 91.34%
Northumbrian Water | Longnewton STW | 254/1940 | 254/1940-02 |  |  | 431.9672 | 53 | 99.98% | Point changed to logger from install on 25/11/20.
Northumbrian Water | Love Avenue Cottages CSO | 226/1258 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Low Fell (TVTE) CSO (G053) | 235/1961 |  |  |  | 0 | 0 | 99.69% | Monitor Installed 19/08/20
Northumbrian Water | Low Hauxley SPS | 224/0961 | 224/0961-02 |  |  | 10 | 3 | 99.98%
Northumbrian Water | Low Heworth Lane SPS | 235/1750 | 235/1750-01 |  |  | 53.5 | 23 | 87.14% | Issue with only a partial dataset being transmitted 10/01/20-15/01/20. Issue occurred again 14/02/20-27/03/20. Cello has been swapped and seems to have resolved the issue.
Northumbrian Water | Low Lane SPS | 241/1080 | 241/1080-01 |  |  | 866.75 | 62 | 99.09%
Northumbrian Water | Low Pittington SPS | 245/1288 | 245/1288-01 |  |  | 749.5 | 46 | 99.97%
Northumbrian Water | Low Southwick SPS | 245/1209 | 245/1209-01 |  |  | 207.25 | 65 | 99.79%
Northumbrian Water | Low Wadsworth SPS | 241/1081 | 241/1081-01 |  |  | 675 | 64 | 97.72%
Northumbrian Water | Low Wadsworth STW | 241/1097 | 241/1097-03 |  |  | 578.3922 | 80 | 100%
Northumbrian Water | Low Willington Park CSO | 243/0983 |  |  |  | 94.25 | 41 | 96.12%
Northumbrian Water | Lowick STW - CSO Inlet | 210/A/0854 | A3 |  |  | 1008.4792 | 73 | 97.94% | Logger installed 01/05/20 but failed on 12/05/20. Back in comms. 03/09/20. Therefore used old digital spill point until 03/09/20.
Northumbrian Water | Lowick STW - Storm Tank | 210/A/0854 | A2 |  |  | 337.8814 | 17 | 99.84% | Installed 03/08/20
Northumbrian Water | Lumley SPS | Permit Anomaly |  |  |  | 42.8256 | 6 | 100%
Northumbrian Water | Lustrum High Level CSO | 254/1830 |  |  |  | 122 | 45 | 98.99%
Northumbrian Water | Lyndhurst Road CSO | 253/1090 |  |  |  | 0 | 0 | 97.37%
Northumbrian Water | Lyndhurst Road CSO | NPSWQD005300 |  |  | Newbiggin North & Newbiggin South | 13.8 | 16 | 99.99%
Northumbrian Water | Lyne CSO (CM045) | 224/0999 |  |  |  | 80 | 32 | 83.67% | Intermittent comms. received traditionally at this site. Comms. generally recover after a maintenance visit, however fail shortly afterwards. Comms. failed between 01/09/20-18/09/20, 30/09/20-14/10/20, 24/10/20-12/11/20 (revisit on 03/11/20 didn't restore comms.), 16/11/20-26/11/20.
Northumbrian Water | Lynemouth STW | 224/0993 | 224/0993-04 |  |  | 2459.2492 | 136 | 99.99%
Northumbrian Water | Lynesack & Softley CSO | 242/1065 |  |  |  | 1.2333 | 2 | 15.18% | Operability <90% due to poor comms. - The monitor requires a site visit to download the data as it's situated in a remote location with poor network coverage and no electricity supply.
Northumbrian Water | Lynwood House CSO (DER44) | 244/1021 |  |  |  | 190.25 | 66 | 98.68%
Northumbrian Water | Lysdon Farm CSO | 226/1196 |  |  | Blyth South Beach | 102.3 | 21 | 92.01%
Northumbrian Water | Mafeking CSO | EPRAB3196VY |  |  |  | 0.5 | 2 | 99.99%
Northumbrian Water | Magdalen Fields South CSO | 210/1362 |  |  |  | 234 | 90 | 97.33%
Northumbrian Water | Magdalene Fields North CSO - High Level M3 Monitoring Point | 210/1355 | A1 |  |  | 0 | 0 | 99.45%
Northumbrian Water | Magdalene Fields North CSO - M2 Monitoring Point | 210/1355 | A1 |  |  | 283 | 76 | 95.65%
Northumbrian Water | Main Street CSO | 223/0951 |  |  |  | 1.25 | 5 | 72.79% | Traditionally a poor site for comms., however this wasn't an issue until 25/09/20. Site has been visited since with a Cello repair however it hasn't recovered. Delay in reinstalling due to unavailability of Point Blues following technical issues.
Northumbrian Water | Main Street CSO | 210/1284 |  |  |  | 0 | 0 | 99.95%
Northumbrian Water | Main Street CSO | 210/1291 |  |  |  | 28.75 | 26 | 99.81%
Northumbrian Water | Main Street CSO | 232/1012 |  |  |  | 0.5 | 1 | 96.05%
Northumbrian Water | Main Street Spittal CSO | 210/1349 |  |  | Spittal | 0 | 0 | 99.99%
Northumbrian Water | Mainsforth Terrace CSO | 255/1208 |  |  |  | 1.5 | 3 | 93.58%
Northumbrian Water | Mainsforth Terrace SPS | 255/1095 | 255/1095-3B |  |  |  |  | 0% | Total number of discharges covered under 255/1095 on the return report reflects discharges via long outfall however there a no separate monitor for the short outfall.
Northumbrian Water | Mainsforth Terrace SPS | 255/1095 | 255/1095-3A |  | Seaton Carew (North) | 61.2614 | 30 | 100%
Northumbrian Water | Manfield STW - CSO Inlet | 252/E/0279 | B |  |  | 2.0653 | 5 | 99.98%
Northumbrian Water | Manfield STW - Network CSO | 252/E/0279 | A |  |  | 110.25 | 40 | 93.24%
Northumbrian Water | Manor Court CSO | 244/0940 |  |  |  | 304.75 | 72 | 99.91%
Northumbrian Water | Manor Gardens South CSO | 235/1965 |  |  |  | 18 | 14 | 96.48%
Northumbrian Water | Marine Drive SPS | 235/1389 | 235/1389-01 |  |  | 0 | 0 | 100%
Northumbrian Water | Marine Parade CSO | 25/06/0984 |  |  | Saltburn Pier | 0.17222 | 1 | 99.99%
Northumbrian Water | Market Lane CSO | 234/0934 |  |  |  | 480.1667 | 63 | 99.99%
Northumbrian Water | Market Lane CSO | 234/1017 |  |  |  | 230 | 58 | 99.21%
Northumbrian Water | Marske STW | 25/06/1015 | 25/06/1015-05 |  | Marske | 15.7697 | 4 | 100%
Northumbrian Water | Marton Ave No 1 (M 023) | 25/04/1600 | 25/04/1600-1 |  |  | 0.5 | 2 | 99.99%
Northumbrian Water | Marton Ave No 2 (M 018) | 25/04/1600 | 25/04/1600-2 |  |  | 7.75 | 6 | 99.99%
Northumbrian Water | Mary Magdalene (No 3) CSO | 233/1250 |  |  |  | 71.2667 | 48 | 99.99%
Northumbrian Water | Maughan Close CSO | 243/1001 |  |  |  | 2 | 6 | 99.99%
Northumbrian Water | Mayfair Road CSO (Dl020) | 253/1274 |  |  |  | 0.5 | 2 | 99.99%
Northumbrian Water | Mayfield Avenue CSO (NC034) | 233/1268 |  |  |  | 24.2333 | 23 | 99.99%
Northumbrian Water | Mayfield CSO | 243/0972 |  |  |  | 172 | 61 | 99.73%
Northumbrian Water | McClean Avenue CSO (Ref L15) | 254/1915 |  |  |  | 63 | 20 | 99.69%
Northumbrian Water | Meadow View CSO | NPSWQD003443 |  |  |  | 0 | 0 | 98.66%
Northumbrian Water | Melkridge STW | 232/1156 | 232/1156-03 |  |  | 120.8994 | 77 | 100%
Northumbrian Water | Melsonby STW | 25/02/1108 | 25/02/1108-02 |  |  | 1016.0092 | 101 | 99.95%
Northumbrian Water | Memorial Hall CSO | 226/0100 |  |  |  | 202 | 49 | 99.08%
Northumbrian Water | Merry Shields Terrace CSO | 233/1255 |  |  |  | 38 | 28 | 99.92%
Northumbrian Water | Metal Bridge SPS/CSO | 243/1011 | A1 |  |  | 0 | 0 | 99.99%
Northumbrian Water | Metrocentre, Green Car Park | 235/2002 |  |  |  | 249.8794 | 109 | 99.65%
Northumbrian Water | Mickleton STW | 251/0940 | 251/0940-03 |  |  | 1792.8536 | 139 | 100%
Northumbrian Water | Middlesbrough CSO Lawson Industrial Estate | 254/1895 |  |  |  | 171 | 37 | 99.78% | Data provided for additional site not identified on the EDM Tracker as requested by REDACTED letter dated 08/02/21.
Northumbrian Water | Middlesbrough Road SPS | QC.25/04/1585 | QC.25/04/1585-S1 Storm Sewage |  |  | 3.5 | 2 | 99.96%
Northumbrian Water | Middleton Airport Storm Treatment | EPRPB3193VX | A1 |  |  | 1050.2783 | 55 | 99.99%
Northumbrian Water | Middleton One Row CSO | QR.25/04/1540 |  |  |  | 198.5 | 49 | 98.28%
Northumbrian Water | Middleton-In-Teesdale STW - CSO Inlet | 25/01/0919 | 25/01/0919-03 |  |  | 70.5 | 30 | 99.99%
Northumbrian Water | Middleton-In-Teesdale STW - Storm Tank | 25/01/0919 | 25/01/0919-02 |  |  | 1.8386 | 1 | 27.52% | Installed 09/06/20. Logger not yet commissioned hence unvalidated data and due to communication issues low operability.
Northumbrian Water | Mid-Tyne CSO No 3 | 233/D/0207 |  |  |  | 0.25 | 1 | 99.64%
Northumbrian Water | Mid-Tyne Sewerage Scheme | 233/B/0113 |  |  |  | 0.25 | 1 | 99.59%
Northumbrian Water | Milfield STW | 210/1327 | 210/1327-02 |  |  | 32.5 | 31 | 99.71%
Northumbrian Water | Milk Market SPS | 235/1115 | [5 empty] | 0% | Monitor in place, data under review.
Northumbrian Water | Mill Cottage CSO | 232/1000 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Mill Cottages CSO (WV087) | 241/1119 |  |  |  | 13.25 | 22 | 99.29%
Northumbrian Water | Mill Farm CSO | 241/1121 |  |  |  | 1 | 1 | 93.66%
Northumbrian Water | Mill Lane CSO | Permit Anomaly |  |  |  | 97.25 | 26 | 99.71% | Permit anomaly to be corrected.
Northumbrian Water | Mill Lane CSO Skinningrove | 256/1063 |  |  |  | 145.75 | 42 | 99.99%
Northumbrian Water | Mill Strand CSO | 210/1348 | [5 empty] | 0% | Unmonitored at present. Highlighted on the change control form.
Northumbrian Water | Mill Terrace CSO | 25/04/1606 |  |  |  | 1.5 | 5 | 96.66%
Northumbrian Water | Millburngate CSO | 245/1286 |  |  |  | 226 | 46 | 87.63% | General comms. issue in January was rectified within normal timescale. Water ingress between sensor and logger caused corruption and comms. failure from 19/04/20-01/06/20. Therefore the logger sends no data back, but dials in. Difficult to identify these issues, and problem is persistent. Once identified a visit was aborted as traffic management was required. Once arranged problem was resolved.
Northumbrian Water | Millfield CSO | 226/1105 |  |  |  | 3.5 | 6 | 99.97%
Northumbrian Water | Millfield SPS | 210/A/0440 | 210/A/0440-02 |  |  | 91.5517 | 23 | 95.84%
Northumbrian Water | Millhouse Farm CSO | 244/0917 |  |  |  | 11.5 | 12 | 99.34%
Northumbrian Water | Mindrum Terrace CSO | 235/1897 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Mini Golf High Level CSO | 235/1797 |  |  | Whitley Bay | 0 | 0 | 100%
Northumbrian Water | Mitchel Terrace CSO | 235/1822 |  |  |  | 86.75 | 40 | 99.99%
Northumbrian Water | Mitchell Avenue SPS | 221/1075 | 221/1075-01 |  | Seahouses North |  |  | 0% | Monitor in place, data under review.
Northumbrian Water | Mitre Place CSO | 235/1940 |  |  |  | 0 | 0 | 97.44%
Northumbrian Water | Moor Crescent CSO | 245/1256 |  |  |  | 121.25 | 57 | 99.03%
Northumbrian Water | Moor Lane CSO | 226/0454 |  |  |  | 47.5 | 20 | 98.02%
Northumbrian Water | Moor Road South CSO | 235/1959 |  |  |  | 0.75 | 1 | 98.28%
Northumbrian Water | Moor View CSO | 232/1016 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Moorsholm STW | 25/06/1010 | 25/06/1010-02 |  |  | 581.6839 | 109 | 99.77%
Northumbrian Water | Moorside CSO (DER002) | 234/1106 |  |  |  | 0.25 | 1 | 94.11%
Northumbrian Water | Mordon STW | Permit Anomaly |  |  |  | 89.9506 | 26 | 99.48%
Northumbrian Water | Morpeth CSO Tenter Terrace (No.1) CM 021 | 225/1075 |  |  |  | 0 | 0 | 99.99% | Data provided for additional site not identified on the EDM Tracker as requested by REDACTED letter dated 08/02/21.
Northumbrian Water | Morpeth STW - CSO Inlet | 225/1036 | A3 |  |  | 0 | 0 | 100%
Northumbrian Water | Morpeth STW - Storm Tank | 225/1036 | A2 |  |  | 150.9956 | 21 | 100%
Northumbrian Water | Mostyn Terrace CSO | 242/1030 |  |  |  | 1.25 | 3 | 66.8% | Believe signal issues affected three local CSOs in Cockfield in July 2020. Cellos couldn't be restored to full comms. so Point Blues were installed, but due to technical comms. issues, the communications aren't robust and unit is transmitting intermittent data packets, so some data are missing from transmission, reducing operability.
Northumbrian Water | Mount Pleasant CSO (DER41) | 244/1020 |  |  |  | 26.75 | 29 | 99.55%
Northumbrian Water | Mount Road CSO BT003 | 210/1358 |  |  | Spittal | 18 | 24 | 99.99%
Northumbrian Water | Mountford Road CSO | 226/1195 |  |  |  | 15.75 | 11 | 99.99%
Northumbrian Water | Murton CSO | EPRCB3195RW |  |  |  | 0.25 | 1 | 99.99%
Northumbrian Water | Napier Court CSO | 235/1850 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Narrowgate CSO | EPRAB3090RL |  |  |  | 35.75 | 32 | 99.93%
Northumbrian Water | Neasham Ejector Station CSO | 254/E/0204 |  |  |  | 176.0514 | 54 | 96.14% | Point changed to logger from install on 04/01/21.
Northumbrian Water | Neasham Road (Y4) CSO | EPRJB3293DK |  |  |  | 1 | 3 | 99.99%
Northumbrian Water | Neasham Road (Y5) CSO | EPRMB3892AA |  |  |  | 18.75 | 29 | 99.99%
Northumbrian Water | Nelson Village CSO | 226/1235 |  |  |  | 60.5 | 17 | 99.98%
Northumbrian Water | Nenthead STW | 232/1097 | 232/1097-03 |  |  |  |  | 0% | Monitor present, although data is not to our reporting standard and an investigation in place to address matter.
Northumbrian Water | Netherton CSO | 223/0872 |  |  |  | 6.75 | 15 | 99.99%
Northumbrian Water | Netherton Park SPS | 226/1278 | 226/1278-01 |  |  | 137.8533 | 9 | 99.99%
Northumbrian Water | Netherton STW | 223/1000 | 223/1000-02 |  |  | 1.3625 | 1 | 99.99%
Northumbrian Water | New Coatham CSO (Ref L73) | 256/1065 |  |  | Redcar Coatham | 38.6667 | 22 | 99.99%
Northumbrian Water | New Hall Farm CSO | 223/0922 |  |  |  | 140 | 52 | 95.87%
Northumbrian Water | New Mare Close Farm CSO | NPSWQD006839 |  |  |  | 124 | 40 | 99.99%
Northumbrian Water | New Moors STWs | 242/A/0706 | A2 |  |  | 248.1722 | 66 | 92.94% | Installed 06/04/20
Northumbrian Water | New Quay CSO (NC058) | 235/1903 |  |  |  | 55 | 25 | 99.15%
Northumbrian Water | New Road CSO | 235/1572 |  |  |  | 22.75 | 15 | 99.22%
Northumbrian Water | New Welbeck Road SPS | 235/1755 | 235/1755-01 |  |  | 364.5 | 55 | 98.77%
Northumbrian Water | New York CSO | 235/1901 |  |  |  | 7 | 6 | 98.46%
Northumbrian Water | Newbiggin CSO (Wilkie Terrace) | 224/0881 |  |  |  | 16.5 | 3 | 93%
Northumbrian Water | Newbiggin/Ashington STW | 225/1031 | A2 |  | Newbiggin North & Newbiggin South |  |  | 0% | Monitor in place, data under review.
Northumbrian Water | Newbiggin/Ashington STW | 225/1031 | A3 |  | Newbiggin North & Newbiggin South |  |  | 0% | Monitor in place, data under review.
Northumbrian Water | Newbrough SPS | 232/0969 | A |  |  | 68.2119 | 31 | 100%
Northumbrian Water | Newburn CSO Burwell Avenue (No.19) NC028 | 235/1877 |  |  |  | 96.75 | 41 | 99.98% | Data provided for additional site not identified on the EDM Tracker as requested by REDACTED letter dated 08/02/21.
Northumbrian Water | Newburn Haugh/Riversdale Way SPS | 235/1731 | 235/1731-01 |  |  | 15 | 3 | 88.04% | Comms failure between 22/10/20-04/12/20 that wasn't fixed on first visit, hence extended downtime.
Northumbrian Water | Newburn Industrial Estate SPS | 235/1732 | 235/1732-01 |  |  | 0 | 0 | 100%
Northumbrian Water | Newburn SPS | 233/1163 | 233/1163-01 |  |  | 24.3944 | 16 | 100%
Northumbrian Water | Newcastle Upon Tyne CSO, St Anne's Wharf | EPRCB3097AS |  |  |  | 487.2833 | 86 | 99.72% | Changed to 2 minute logging 18/05/20.
Northumbrian Water | Newfield Farm CSO | EPRCB3191WN |  |  |  | 0 | 0 | 96.74%
Northumbrian Water | Newfield STW | 243/1015 | 243/1015-02 |  |  | 150.4025 | 41 | 100% | Installed 16/04/20
Northumbrian Water | Newholme CSO (Ref TE103) | 25/02/1103 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Newport Road CSO | 254/1863 |  |  |  | 36.1206 | 29 | 99.99%
Northumbrian Water | Newport SPS | 254/0255 | 254/0255-01 |  |  | 0.055278 | 2 | 100%
Northumbrian Water | Newton Street CSO | 235/1367 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Nicky Nack SPS | 243/0933 | 243/0933-01 |  |  | 22.2397 | 20 | 100%
Northumbrian Water | Nightingale Place CSO | 245/1311 |  |  |  | 193.5 | 60 | 99.48%
Northumbrian Water | No 2 Eskdale Gardens CSO | 235/1442 |  |  |  | 55.25 | 41 | 98.43%
Northumbrian Water | No.20 Derwentdale (Cutlers Rd) | 234/1113 |  |  |  | 0.25 | 1 | 98.55%
Northumbrian Water | Norham STW | 210/1328 | 210/1328-04 |  |  | 314.0594 | 25 | 99.97%
Northumbrian Water | North Blyth SPS | 226/1156 | 226/1156-01 |  |  | 70.8208 | 16 | 100%
Northumbrian Water | North Cambois SPS | 226/1155 | 226/1155-01 |  |  | 0 | 0 | 100% | Installed 30/12/20
Northumbrian Water | North Gosforth CSO | 226/1253 |  |  |  | 38 | 29 | 99.04%
Northumbrian Water | North Groyne SPS | 235/1481 | A |  |  | 5.7808 | 10 | 100%
Northumbrian Water | North Hylton CSO & SPS | 245/0938 | 245/0938-01 |  |  | 71.6822 | 28 | 99.96%
Northumbrian Water | North Parade High Level CSO | 235/1795 |  |  | Whitley Bay | 8.5786 | 6 | 100%
Northumbrian Water | North Point CSO (NTY049) | 235/1987 |  |  | Cullercoats | 0 | 0 | 100%
Northumbrian Water | North Seaton CSO (WK031) | 225/1063 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | North Seaton Level Crossing CSO | 225/1020 |  |  |  | 150.25 | 42 | 99.78%
Northumbrian Water | North Tees SPS | 254/0057 | 254/0057-01 |  |  | 161.8214 | 28 | 100% | Point changed to logger from install on 24/11/20.
Northumbrian Water | North Wylam SPS | 233/D/0206 | A1 |  |  | 48.6 | 33 | 98.37%
Northumbrian Water | Northside Place CSO | 226/1264 |  |  |  | 0.25 | 1 | 98.66%
Northumbrian Water | Norton SPS | 254/B/0252 | 254/B/0252-01 |  |  | 38.4833 | 13 | 100%
Northumbrian Water | Nunthorpe No.1 SPS | 25/04/1621 | S1 |  |  | 218.5161 | 20 | 100%
Northumbrian Water | Oak Road CSO | 256/1064 |  |  | Redcar Stray | 0 | 0 | 99.99%
Northumbrian Water | Oakenshaw CSO (WV065) | 243/1005 |  |  |  | 1 | 4 | 93.14%
Northumbrian Water | Oakfield Road CSO | 254/1207 |  |  |  | 9.5 | 6 | 99.99%
Northumbrian Water | Oakley Green CSO | Permit Anomaly |  |  |  | 49.75 | 34 | 99.4% | Permit anomaly to be corrected.
Northumbrian Water | Oaks Field SRT CSO | 235/1710 |  |  |  | 35.75 | 16 | 99.85%
Northumbrian Water | Ogle STW | Permit Anomaly |  |  |  | 0.94194 | 4 | 99.22% | Installed 17/04/20
Northumbrian Water | Old Castleside STW CSO | 234/1135 |  |  |  | 32.5 | 18 | 95.05%
Northumbrian Water | Old Cleatlam STW | Permit Anomaly | [5 empty] | 0% | Unmonitored in 2020. Monitor installed 12/02/21. Investigation to address the matter required.
Northumbrian Water | Old Cornforth Sewage SPS | 243/0602 | 243/0602-01 |  |  | 53.5 | 16 | 99.72%
Northumbrian Water | Old Derwent Bridge CSO | 234/0904 |  |  |  | 23.75 | 13 | 94.52%
Northumbrian Water | Old Hall CSO | 223/G/0102 |  |  |  | 53 | 24 | 99.23%
Northumbrian Water | Old River Tees SPS | 254/1937 | [5 empty] | 0% | Monitor installed but data not recovered. Investigation undertaken.
Northumbrian Water | Old Tyne Bridge CSO | 232/1166 |  |  |  | 74 | 54 | 99.52%
Northumbrian Water | Old Yarm STW Site SPS | 254/1092 | A (Settled storm) |  |  | 325.25 | 33 | 99.99%
Northumbrian Water | Oliver Street CSO | 245/1265 |  |  |  | 0 | 0 | 97.71%
Northumbrian Water | Opposite No. 16 Front Street CSO | EPRBB3899DP |  |  |  | 29.5 | 26 | 99.95%
Northumbrian Water | Osman Terrace CSO | 245/1378 |  |  |  | 37.5 | 6 | 99.8%
Northumbrian Water | Otterburn Crescent CSO | 245/1367 |  |  |  | 1 | 2 | 99.99%
Northumbrian Water | Otterburn STW | 231/1087 | 231/1087-02 |  |  | 1835.6661 | 104 | 100%
Northumbrian Water | Ouse Burn CSO No 8 | 235/F/0346 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Ouseburn East SPS | 235/1825 | 235/1825-01 |  |  | 29.7006 | 20 | 100%
Northumbrian Water | Ouseburn West SPS | 235/1824 | 235/1824-01 |  |  | 66.3694 | 5 | 7.694% | Issues with operability of sensor as it is an overflow float and this site receives tidal ingress. Awaiting a logger install.
Northumbrian Water | Ouston Villas Farm (NE) CSO | 235/1878 |  |  |  | 42.5 | 13 | 99.99%
Northumbrian Water | Outlet Lane CSO | 233/1050 |  |  |  | 0 | 0 | 99.98%
Northumbrian Water | Outlet Road No2 CSO (TD031) | 233/1240 |  |  |  | 5.75 | 1 | 91.46%
Northumbrian Water | Ovingham SPS CSO & Emergency | 233/G/0328 | A1 |  |  | 34.25 | 12 | 99.9%
Northumbrian Water | Ovington STW CSO | 252/E/0329 |  |  |  | 67.3211 | 12 | 78.36% | Installed 24/04/20. Logged until 17/07/20, comms. failed and revisited on 04/09/20.
Northumbrian Water | Ovington TD034 CSO | 233/1248 |  |  |  | 58.8069 | 42 | 99.27%
Northumbrian Water | Owen Brannigan Drive CSO | 226/1260 |  |  |  | 0.5 | 2 | 99.77%
Northumbrian Water | Owton Manor Lane CSO | QR.25/05/5014 |  |  | Seaton Carew (Centre) | 0.033333 | 1 | 99.68% | Bathing Water data reviewed. 4x12/24 discharges of total duration 28.6 hours reported in Bathing Water season were spurious and removed from whole year submission. Bathing Water operability of 99.98% recalculated as 99.18% for the Bathing Water season.
Northumbrian Water | Oxbridge Lane CSO (ST024) | 254/1835 |  |  |  | 81.25 | 20 | 99.02%
Northumbrian Water | Palace Street North CSO-1 | 210/1361 |  |  | Spittal | 4.3667 | 21 | 99.99%
Northumbrian Water | Palace Street North CSO-2 | 210/1357 |  |  | Spittal | 3.4667 | 14 | 99.73%
Northumbrian Water | Pallion SPS | 245/1210 | 245/1210-01 |  |  | 54.25 | 39 | 99.99%
Northumbrian Water | Palm Terrace CSO | 235/1717 |  |  |  | 0 | 0 | 92.64%
Northumbrian Water | Paradise Farm (Willows Farm) | 243/0988 | A1 |  |  | 26 | 15 | 99.82%
Northumbrian Water | Paradise Farm CSO (EA063) | 255/1217 |  |  |  | 120.75 | 44 | 99.82%
Northumbrian Water | Park Head Storage Tank CSO | 242/1044 |  |  |  | 81 | 15 | 99.97%
Northumbrian Water | Park Hill CSO | 243/1013 |  |  |  | 25 | 19 | 99.63%
Northumbrian Water | Park Lane CSO | 256/1080 |  |  |  | 42.0586 | 27 | 100%
Northumbrian Water | Park Road & Green Lane CSO | 225/G/0361 |  |  |  | 4.5 | 6 | 99.84%
Northumbrian Water | Park Road CSO | NPSWQD009544 |  |  |  | 143 | 34 | 99.78%
Northumbrian Water | Park Road CSO (WV41) | 241/1034 |  |  |  | 0 | 0 | 86.81% | Comms. failed 17/11/20-end of year. New unit had been installed on 21/08/20 but due to technical communications issues intermittent comms have been received and with there being no resolution yet contractor are aware a revisit is required, however this hasn't been completed.
Northumbrian Water | Park Road North CH070 | 245/1264 |  |  |  | 8.5 | 10 | 99.99%
Northumbrian Water | Parkgate Farm CSO (G028) | 234/1131 |  |  |  | 0.25 | 1 | 99.99%
Northumbrian Water | Pasture Lane CSO (L001) | 25/04/1776 |  |  |  | 22.5 | 12 | 95.28%
Northumbrian Water | Patton Street CSO | 255/1193 |  |  |  | 22.5 | 5 | 56.78% | New install. Had a Cello installed, now switched to Point Blue, however this is awaiting resolution of technical issues. Comms. failed 20/06/20-05/07/20, 14/07/20-15/07/20, 16/09/20-end of year.
Northumbrian Water | Pearson Street CSO (SE009) | 243/1000 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Peases West CSO | 241/1083 |  |  |  | 295.75 | 50 | 97.93%
Northumbrian Water | Pegswood CSO County First School | EPRCB3192AA |  |  |  | 8.5 | 17 | 99.95%
Northumbrian Water | Pegswood STW | 225/1079 | A2 |  |  | 151.0647 | 19 | 100%
Northumbrian Water | Pelaw Bank CSO (CH57) | 245/1323 |  |  |  | 168 | 63 | 98.53%
Northumbrian Water | Pelaw Wood St. Giles Close Durham CSO | EPRBB3691AB |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Pelton CSO | 245/E/0391 |  |  |  | 1 | 4 | 93.27%
Northumbrian Water | Pelton CSO Wheldon Terrace Ch 018 | EPR/AB3894VG |  |  |  | 0 | 0 | 99.01% | Data provided for additional site not identified on the EDM Tracker as requested by REDACTED letter dated 08/02/21.
Northumbrian Water | Pelton Fell Road 3 CSO (CH14) | 245/1314 |  |  |  | 111 | 51 | 99.99%
Northumbrian Water | Pelton Fell Road CSO | 245/1335 |  |  |  | 71.75 | 29 | 92.9%
Northumbrian Water | Pennine View CSO | 234/1161 |  |  |  | 30.75 | 12 | 99.99%
Northumbrian Water | Percy Main CSO | 235/1900 |  |  |  | 4.25 | 7 | 81.43% | Regularly suffers from water ingress and connection between sensor and logger becomes corrupt. Therefore the logger sends no data back, but dials in. Difficult to identify these issues, and problem is persistent. Issue from 17/03/20-09/04/20 and 17/04/20-21/04/20. Comms. failed 04/05/20-10/06/20, 31/07/20-04/08/20.
Northumbrian Water | Percy Road High Level CSO | 235/1794 |  |  | Whitley Bay | 0 | 0 | 99.99%
Northumbrian Water | Pesspool Lane CSO | 255/1179 |  |  |  | 234.9 | 25 | 99.89%
Northumbrian Water | Peth Head SPS | Permit Anomaly |  |  |  | 207.5164 | 68 | 99.99%
Northumbrian Water | Philipburn Dene SPS | 232/A/1011 |  |  |  | 65.6114 | 23 | 100%
Northumbrian Water | Phillipson Street CSO | EPRBB3897EY |  |  |  | 55.25 | 36 | 97.78% | Monitor present, although data is not to our reporting standard and an investigation in place to address matter as this is over reporting.
Northumbrian Water | Pilot Station SPS | 235/0076 | 235/0076-01 |  |  | 15.5903 | 15 | 99.96%
Northumbrian Water | Pinewood Gardens CSO | 235/1968 |  |  |  | 23.75 | 26 | 99.84%
Northumbrian Water | Pipewellgate SPS | 235/1664 | 235/1664-01 |  |  | 0 | 0 | 99.21%
Northumbrian Water | Pithouse Lane CSO (West Rainton No.5) | EPRGB3599NT |  |  |  | 138.75 | 42 | 91.67%
Northumbrian Water | Pittington STW | 245/0842 |  |  |  | 860.6869 | 71 | 100%
Northumbrian Water | Pity Me Roundabout CSO | 245/1354 |  |  |  | 91.5 | 23 | 99.37%
Northumbrian Water | Pity Me STW | 245/1274 | 245/1274-03 |  |  | 100.1278 | 26 | 100%
Northumbrian Water | Plawsworth CSO MH1 | 245/E/0213 |  |  |  | 81.75 | 46 | 98.29%
Northumbrian Water | Plawsworth STW | 245/A/0713 |  |  |  | 6.13/2.15 | 6/3 | 45.93%/8.82% | Installed 18/11/2020. Loggers not yet commissioned hence unvalidated data and due to communication issues low operability.
Northumbrian Water | Playing Field CSO | 243/0991 |  |  |  | 0.5 | 2 | 98.98%
Northumbrian Water | Point A Damside CSO (CM022) | 225/1064 |  |  |  | 78 | 24 | 87.05% | Suffered from water ingress and connection between sensor and logger became corrupt. Therefore the logger sent no data back, but dialled in. Difficult to identify these issues, and problem is persistent. Issue between 29/09/20-03/11/20. It was visited on 09/10/20 however comms. weren't restored on first visit. Period of data loss between 10/12/20-22/12/20 as well.
Northumbrian Water | Point L the Kylins CSO | 225/1065 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Point Pleasant SPS | 235/1691 | 235/1691-01 |  |  | 0 | 0 | 100%
Northumbrian Water | Pont Bungalows CSO (DER130) | 234/1141 |  |  |  | 0 | 0 | 98.08%
Northumbrian Water | Pont Lane A CSO | 234/1054 |  |  |  | 36.5 | 14 | 99.98%
Northumbrian Water | Pont Lane B CSO | 234/1055 |  |  |  | 62.5 | 26 | 97.12%
Northumbrian Water | Port Clarence West SPS | QR.25/04/1542 | S1 |  |  | 0.37889 | 3 | 100% | Point changed to logger from install on 03/11/20.
Northumbrian Water | Portrack STW - CSO Inlet | 25/04/1657 | 25/04/1657-02 |  |  | 282.9267 | 40 | 88.8% | Point changed to logger from install on 06/10/20. Logger failed twice in commissioning period (13/08/20-04/09/20 & 17/09/20-06/10/20).
Northumbrian Water | Portrack STW - Storm Tank | 25/04/1657 | 25/04/1657-01 |  |  | 370.0681 | 61 | 99.99%
Northumbrian Water | Potter Street SPS | 235/1688 | 235/1688-01 |  |  | 2.4986 | 2 | 100%
Northumbrian Water | Pottery Lane CSO & SPS | 245/1171 | 245/1171-01 |  |  | 200.7964 | 28 | 99.99%
Northumbrian Water | Powburn STW | 210/1295 | 210/1295-02 |  |  | 1184.695 | 84 | 99.96% | Point upgraded from 16/12/20.
Northumbrian Water | Priestlands Close CSO | 233/1256 |  |  |  | 0 | 0 | 99.44%
Northumbrian Water | Priestley Crescent CSO | 245/1386 |  |  |  | 26 | 32 | 97.28%
Northumbrian Water | Prince Consort Road SPS | 235/1657 | 235/1657-01 |  |  | 82 | 40 | 99.93%
Northumbrian Water | Princess Anne Park CSO SU003 | 245/1334 |  |  |  | 2.9333 | 6 | 99.99%
Northumbrian Water | Priory Road CSO | 254/1862 |  |  |  | 53.25 | 28 | 99.56%
Northumbrian Water | Prissick CSO | QR.25/04/1575 |  |  |  | 0 | 0 | 99.45%
Northumbrian Water | Prudhoe CSO 4 | 233/G/0117 |  |  |  | 11.3833 | 12 | 97.9% | Changed to 2 minute logging 18/05/20.
Northumbrian Water | Prudhoe SPS & CSO | 233/0974 | A1 |  |  | 37.25 | 6 | 98.28%
Northumbrian Water | Quarry Heads Lane CSO | 245/E/0409 |  |  |  | 0.25 | 1 | 90.88%
Northumbrian Water | Quarry Lane CSO | 242/D/0075 |  |  |  | 40 | 18 | 99.98%
Northumbrian Water | Quarry Plantation (Above Clifton Gardens) | EPRNB3990VN |  |  |  | 3.9333 | 5 | 98.84% | Changed to 2 minute logging 18/05/20.
Northumbrian Water | Quayside (Hillgate Street) CSO | EPRBP3721GX |  |  |  | 0 | 0 | 98.58%
Northumbrian Water | Quayside/St Lawrence Road CSO | 235/1766 |  |  |  | 0.033333 | 1 | 97.81%
Northumbrian Water | Quebec SPS | 244/A/0456 | 244/A/0456-02 |  |  | 48.1333 | 24 | 99.99%
Northumbrian Water | Queen Alexandra Bridge CSO & SPS | 245/0928 | 245/0928-01 |  |  | 78.4925 | 37 | 99.98%
Northumbrian Water | Queen Street (Allotments) CSO | 25/04/1777 |  |  |  | 6 | 10 | 99.99%
Northumbrian Water | Queens Gardens CSO | 210/1007 |  |  | Spittal | 78.7333 | 50 | 99.98%
Northumbrian Water | Queensport Close CSO (ST057) | 254/1829 |  |  |  | 78.5 | 20 | 98.82%
Northumbrian Water | Queensway CSO (DER169) | 234/1134 |  |  |  | 0 | 0 | 99.97%
Northumbrian Water | R Gill Lockhaugh Road & Sherburn Park CSO | 234/1130 |  |  |  | 8.75 | 6 | 99.97%
Northumbrian Water | Raby Avenue CSO | 252/1123 |  |  |  | 5.25 | 3 | 99.99%
Northumbrian Water | RAF Boulmer SPS | 221/1036 | 221/1036-01 |  |  | 28.6172 | 9 | 99.82%
Northumbrian Water | Railway Gardens CSO (DER047) | 235/1930 |  |  |  | 14.25 | 11 | 99.87%
Northumbrian Water | Railway Line CSO | 243/1014 |  |  |  | 73.9667 | 41 | 99.99%
Northumbrian Water | Railway St CSO | 244/0938 |  |  |  | 89.5 | 39 | 99.37%
Northumbrian Water | Railway Station (east of) TD040 Stocksfield CSO | 233/D/0068 |  |  |  | 17.5 | 11 | 99.88%
Northumbrian Water | Railway Street CSO | 210/1350 |  |  | Spittal | 1.6667 | 9 | 99.94%
Northumbrian Water | Ramshaw SPS | 242/1007 | 242/1007-01 |  |  | 4.25 | 7 | 85.55% | Intermittent comms. location. No comms. 05/01/20-16/01/20, 27/03/20-08/04/20, 24/04/20-30/04/20. Due to water ingress connection between sensor and logger became corrupt. Therefore the logger sent no data back between 12/10/20-04/11/20.
Northumbrian Water | Ramshaw STW - CSO Inlet | 242/1071 | A3 |  |  | 239.8794 | 35 | 99.01% | Installed 12/06/20
Northumbrian Water | Ramshaw STW - Storm Tank | 242/1071 | A2 |  |  | 558.6308 | 29 | 99.93%
Northumbrian Water | Ravenscroft Avenue CSO | 254/1922 |  |  |  | 7.25 | 3 | 99.71%
Northumbrian Water | Ravensdowne Barracks SPS | 210/1251 | 210/1251-01 |  | Spittal | 0 | 0 | 99.9%
Northumbrian Water | Rear 10 Burnett Crescent CSO | 243/0990 |  |  |  | 15.25 | 14 | 99.99%
Northumbrian Water | Rear 3 Ernest Street CSO | EPRAB3390WN |  |  |  | 1.5 | 2 | 99.68%
Northumbrian Water | Rear 39 Cutlers Hall Road CSO | 234/1133 |  |  |  | 0.5 | 2 | 98.94%
Northumbrian Water | Rear 92/94 Charles Street CSO | EPRAB3290DW |  |  |  | 0 | 0 | 99.41%
Northumbrian Water | Rear 95/97 Charles Street CSO | EPRAB3291RT |  |  |  | 3 | 2 | 99.99%
Northumbrian Water | Rear 97/99 Arnold Street CSO | EPRAB3290EA |  |  |  | 0 | 0 | 93.2%
Northumbrian Water | Rear Foster St Easson Road CSO | EPRBB3699VN |  |  |  | 0.25 | 1 | 99.99%
Northumbrian Water | Rear of Third St CSO (EA072) | 255/1211 |  |  |  | 0.5 | 2 | 98.98%
Northumbrian Water | Rear of Well House Farm CSO- Dl25 | NPSWQD009688 |  |  |  | 10.25 | 14 | 99.89%
Northumbrian Water | Rear St Michaels CSO | 245/1316 |  |  |  | 3.75 | 5 | 99.99%
Northumbrian Water | Rectory Cottage CSO | 243/0971 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Red Barns SPS | 221/1069 | 221/1069-01 |  | Bamburgh Castle | 3.3819 | 2 | 100%
Northumbrian Water | Red Row SPS | 224/A/0616 | A1 |  |  | 36.2319 | 9 | 100%
Northumbrian Water | Redburn SPS | 232/1170 | 232/1170-02 |  |  | 4.1475 | 28 | 99.99%
Northumbrian Water | Redwell Lane SPS | 235/1588 | 235/1588-02 |  | Marsden | 54.1667 | 21 | 99.99%
Northumbrian Water | Redworth Hall SPS | 253/D/0204 | A1 |  |  | 37.685 | 15 | 99.96%
Northumbrian Water | Rennington SPS | 221/1066 | 221/1066-01 |  |  | 33.1597 | 9 | 99.99%
Northumbrian Water | Renny's Lane SPS | 245/A/0464 | 245/A/0464-02 |  |  | 14.3308 | 8 | 100%
Northumbrian Water | Reyrolle Sewer (South) CSO | 235/1186 |  |  |  | 152.25 | 67 | 99.29%
Northumbrian Water | Richard Street SPS | 256/1075 | 256/1075-01 |  |  | 1.5 | 5 | 99.98%
Northumbrian Water | Riding Dene CSO | 233/G/0178 |  |  |  | 6.5667 | 13 | 99.16%
Northumbrian Water | Riding Mill Village SPS | 233/1040 | 233/1040-01 |  |  | 348.7308 | 33 | 98.17% | Point upgraded from 26/11/20.
Northumbrian Water | Ridley Mill Road CSO | 233/1254 |  |  |  | 22.5 | 6 | 99.81%
Northumbrian Water | Ridley Street SPS | 226/1175 | 226/1175-01 |  |  | 0 | 0 | 100%
Northumbrian Water | River Walk CSO | 242/1062 |  |  |  | 1 | 4 | 99.99%
Northumbrian Water | Riversdale Road CSO | 235/1365 |  |  |  | 0.33333 | 4 | 99.99%
Northumbrian Water | Riverside CSO | 241/1091 |  |  |  | 61.75 | 51 | 99.32%
Northumbrian Water | Riverside CSO | 242/1043 |  |  |  | 402 | 62 | 99.73%
Northumbrian Water | Riverside Way CSO | EPRCB3191VZ |  |  |  | 178.5928 | 32 | 99.73%
Northumbrian Water | Roker CSO | 245/1109 |  |  | Roker (Whitburn South) | 0 | 0 | 100%
Northumbrian Water | Romaldkirk STW - CSO Inlet | 25/01/0912 | 25/01/0912-04 |  |  |  |  | 0% | Installed 30/03/20. To be re-commissioned. Investigation to address the matter required.
Northumbrian Water | Romaldkirk STW - Storm Tank | 25/01/0912 | 25/01/0912-03 |  |  | 540.2792 | 75 | 99.94%
Northumbrian Water | Roman Road CSO | 235/1703 |  |  |  | 132.75 | 33 | 99.04%
Northumbrian Water | Rookhope STW | 241/1145 | 241/1145-02 |  |  | 793.2219 | 81 | 99.99%
Northumbrian Water | Ropery Lane/Eardulph Avenue CSO | 245/1088 |  |  |  | 0 | 0 | 83.64% | Maintenance request raised early June, but site requires traffic management which wasn’t arranged until late July, hence low operability during this time. Comms. failed 02/06/20-30/07/20.
Northumbrian Water | Rose Cottage SPS | 233/1220 | 233/1220-01 |  |  | 137 | 39 | 99.62%
Northumbrian Water | Rose Crescent CSO | 245/1096 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Rose Street CSO | 235/1917 |  |  |  | 12.2581 | 20 | 99.9%
Northumbrian Water | Rose Terrace CSO | 241/1089 |  |  |  | 7.25 | 12 | 99.99%
Northumbrian Water | Roseleigh CSO | 233/1055 |  |  |  | 24.25 | 22 | 98.4%
Northumbrian Water | Rothbury STW | 223/0820 | A2 |  |  | 24.6211 | 11 | 87.42% | Installed 17/04/20. Logger failed 01/11/20. Maintenance request raised 20/10/20. Attended 30/11/20.
Northumbrian Water | Rough Lea Lane CSO (WV79) | 243/0909 |  |  |  | 11.75 | 14 | 95.81%
Northumbrian Water | Rowan Drive CSO (DU52) | 245/1326 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Rowlandson Terrace CSO | 253/1080 |  |  |  | 7 | 14 | 71.15% | Period of poor data received from 06/05/20-12/05/20 reducing operability. Logger started sending sporadic bursts of data from 01/09/20-23/12/20. Point Blue installed on 30/09/20 however due to technical issues communications still poor.
Northumbrian Water | Rushyford SPS & CSO | 253/0600 | 253/0600-03 |  |  | 226 | 28 | 99.72%
Northumbrian Water | Russell Place CSO (Rosedale Allotments) Rear Victoria Street CSO (WV068) | 243/1007 |  |  |  | 81.5 | 31 | 99.93%
Northumbrian Water | Rutland St/Leeholme Road CSO | 253/1260 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Ryhope CSO | 255/1200 | [5 empty] | 0% | Unmonitored at present. Highlighted on the change control form.
Northumbrian Water | Sacriston STW | 245/1254 | 245/1254-03 |  |  | 1246.0306 | 99 | 100%
Northumbrian Water | Sadberge SPS | 25/04/1749 | 25/04/1749-01 |  |  | 1.5 | 5 | 97.87%
Northumbrian Water | Sadberge STW | 25/03/1235 | 25/03/1235-02 |  |  | 8.0722 | 3 | 84.94% | Installed 28/10/20. Logger failed 07/12/20-16/12/20.
Northumbrian Water | Salisbury Road SPS | Permit Anomaly |  |  |  | 10.1003 | 11 | 100%
Northumbrian Water | Salters Lane CSO | 235/1895 |  |  |  | 140.1514 | 31 | 100%
Northumbrian Water | Saltmeadows SPS | 235/1195 | 235/1195-01 |  |  | 0 | 0 | 99.99%
Northumbrian Water | Sandgate CSO | 210/0935 |  |  | Spittal | 150.0994 | 64 | 96.17%
Northumbrian Water | Sands Syphon CSO | 245/0906 |  |  |  | 213.25 | 43 | 87.75% | Comms. failed 18/11/20-end of year. Was visited on 27/11/20 however SIM card wouldn't dial out on old unit. Stock of new units required before it could be rescheduled.
Northumbrian Water | Satley STW | 244/A/0494 |  |  |  | 6.6253 | 15 | 99.09% | Installed 24/04/20
Northumbrian Water | Scorer's Lane CSO | 245/1307 |  |  |  | 4.25 | 5 | 99.99%
Northumbrian Water | Scotch Isle Farm CSO (WV085) | 241/1120 |  |  |  | 35.75 | 34 | 96.62%
Northumbrian Water | Scots Gap STW | 225/A/0871 |  |  |  | 44.7619 | 14 | 46.53% | Installed 08/06/20. Logger lost comms. during commissioning period from 29/08/20-16/12/20.
Northumbrian Water | Scotswood Bridge CSO | 235/1669 |  |  |  | 0 | 0 | 99.72% | Changed to 2 minute logging 04/03/20.
Northumbrian Water | Scotswood Road No.01 SPS | 235/1673 | 235/1673-01 |  |  | 0.22556 | 2 | 98.83% | Point changed to logger from install on 08/10/20.
Northumbrian Water | Scotswood Road No.03 SPS | 235/1668 | 235/1668-01 |  |  | 23.5 | 28 | 99.96%
Northumbrian Water | Scotswood Road No.04 SPS | 235/1667 | 235/1667-01 |  |  | 0 | 0 | 100%
Northumbrian Water | Scotswood SPS at Vickers | 235/1670 | 235/1670-01 |  |  | 0 | 0 | 99.65%
Northumbrian Water | Scout House Farm 1 CSO | 244/0998 |  |  |  | 147.25 | 23 | 99.7%
Northumbrian Water | Scout House Farm 2 CSO | 244/1005 |  |  |  | 5.75 | 10 | 99.43%
Northumbrian Water | Scremerston No 1 SPS | 210/0880 |  |  |  | 50.9119 | 15 | 100%
Northumbrian Water | Scremerston No 2 SPS | 210/0880 |  |  |  | 370.7669 | 58 | 99.98%
Northumbrian Water | Sea Road CSO | EPRPP3227GJ |  |  | Spittal | 0 | 0 | 96.45%
Northumbrian Water | Sea View CSO | 224/0994 |  |  |  | 292 | 61 | 94.19%
Northumbrian Water | Sea View Walk Storage Tank CSO | 255/1178 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Seaburn North CSO | 245/1107 |  |  | Seaburn (Whitburn North) | 0 | 0 | 99.99%
Northumbrian Water | Seaburn South CSO | 245/1108 |  |  | Seaburn (Whitburn North) | 0 | 0 | 99.99%
Northumbrian Water | Seaham CSO No 8 | 255/E/0620 |  |  | Seaham Hall | 3.3333 | 14 | 99.99%
Northumbrian Water | Seaham Road CSO (SU35) | 245/1363 |  |  |  | 48.25 | 36 | 99.92%
Northumbrian Water | Seaham South Dock CSO (1302) | EPRYB3835AX |  |  |  | 0 | 0 | 92.07%
Northumbrian Water | Seaham STW | 255/1125 | 255/1125-03 |  |  | 433.9783 | 40 | 100% | Point upgraded from 26/11/20.
Northumbrian Water | Seamer SPS | 254/0981 | A |  |  | 18.0233 | 8 | 99.96%
Northumbrian Water | Seaton Carew STW - CSO Inlet | 254/1966 | 254/1966-05 |  | Seaton Carew (North) | 274.4306 | 72 | 100%
Northumbrian Water | Seaton CSO1 EA003 | 255/E/0645 |  |  |  | 0.75 | 3 | 98.38%
Northumbrian Water | Seaton North Hotel CSO (WK013) | 225/1070 |  |  |  | 113.5 | 45 | 99.59%
Northumbrian Water | Seaton Sluice SPS | 226/0946 | A |  | Seaton Sluice | 76.2289 | 12 | 97.82%
Northumbrian Water | Sedgefield STW | 254/1864 | 254/1864-04 |  |  | 1221.7361 | 66 | 99.99%
Northumbrian Water | Sedgeletch Bridge CSO | 245/1377 |  |  |  | 26.75 | 22 | 99.98%
Northumbrian Water | Sedgeletch STW - CSO Inlet | 245/1243 | A3 |  |  | 266.6286 | 83 | 100%
Northumbrian Water | Sedgeletch STW - Storm Tank | 245/1243 | A2 |  |  | 0.47611 | 1 | 0.1715% | Point changed to logger from install on 31/12/20. Original point identified was inaccurate so all data marked invalid and inoperable until logger was installed.
Northumbrian Water | Seghill CSO | 226/F/0419 |  |  |  | 9.9333 | 29 | 99.91% | Set to 2 minutes to resolve data spikes.
Northumbrian Water | Seymour Crescent (Hunters Rest) CSO | 254/1824 |  |  |  | 2.2242 | 6 | 100%
Northumbrian Water | Sharpness Point SPS | 235/1582 | 235/1582-01 |  | Tynemouth Longsands South | 0.32861 | 4 | 100% | Point changed to logger from install on 15/01/21.
Northumbrian Water | Sheraton CSO | 235/A/0509 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Sherburn CSO Manhole No 32 | 245/E/0511 |  |  |  | 1.75 | 4 | 98.56%
Northumbrian Water | Sherburn CSO Manhole No 34 | 245/E/0513 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Sherburn Near Mill Lane CSO | 245/1297 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Sherburn STW | 245/1248 | 245/1248-03 |  |  | 290.8922 | 58 | 100%
Northumbrian Water | Shibdon Road CSO | 234/1021 |  |  |  | 0.5 | 3 | 99.99%
Northumbrian Water | Shields Road CSO | 245/1114 |  |  |  | 86 | 40 | 95.58%
Northumbrian Water | Shilbottle CSO No 2 A015 | 223/G/0087 |  |  |  | 43.75 | 25 | 97.08%
Northumbrian Water | Shilbottle STW | 223/0991 | 223/0991-02 |  |  | 2205.5372 | 121 | 100% | Point upgraded from 16/12/20.
Northumbrian Water | Shildon CSO | 25/03/1216 |  |  |  | 15 | 10 | 99.99%
Northumbrian Water | Shildon CSO West Road Auckland | EPRAB3691WJ |  |  |  | 0.5 | 2 | 99.99%
Northumbrian Water | Shincliffe (A177) CSO | 245/1285 |  |  |  | 6 | 8 | 99.96%
Northumbrian Water | Shincliffe No 1 SPS & CSO (SSO Manhole No 2) | 245/E/0499 | A1 |  |  | 27.75 | 11 | 99.96%
Northumbrian Water | Shincliffe SPS | 245/A/0463 | 245/A/0463-02 |  |  | 14.9236 | 8 | 100%
Northumbrian Water | Shiney Row Footbridge CSO | 245/1368 |  |  |  | 30.25 | 21 | 99.94%
Northumbrian Water | Shoregate CSO | 210/1347 |  |  | Spittal | 23.5 | 15 | 99.99%
Northumbrian Water | Shotley Bridge CSO | 234/1107 |  |  |  | 138.5 | 36 | 88.97% | Comms. failed 01/09/20-11/09/20 and 05/12/20-end of year. Visited by contractor on 07/12/20 however comms. weren't restored.
Northumbrian Water | Shotley Bridge Hospital CSO | 234/1116 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Shotton Lane CSO | 255/1194 |  |  |  | 159 | 38 | 98.98%
Northumbrian Water | Silver Lonnen CSO (NC030) | 235/1938 |  |  |  | 157.6667 | 56 | 99.97%
Northumbrian Water | Simonside CSO | 226/1124 |  |  | Seaton Sluice | 1.4 | 8 | 99.99%
Northumbrian Water | Sixth St CSO | 244/0873 |  |  |  | 2.5 | 8 | 97.81%
Northumbrian Water | Skinningrove SPS CSO 1 | 25/06/1033 | 25/06/1033-01 |  |  |  |  | 0% | Unmonitored at present. Scheduled to be installed.
Northumbrian Water | Skinningrove SPS CSO 2 | 25/06/1033 | 25/06/1033-02 |  |  | 1.2683 | 1 | 100%
Northumbrian Water | Skippers Lane Industrial Est CSO | 254/1849 |  |  |  | 20.25 | 8 | 99.98%
Northumbrian Water | Slaggyford SPS | 232/0992 | 232/0992-01 |  |  | 102.6069 | 24 | 99.91%
Northumbrian Water | Slaley STW - CSO Inlet | 233/1178 | 233/1178-03 |  |  | 40.0108 | 20 | 100% | Installed 24/04/20
Northumbrian Water | Slaley STW - Primary Treated Storm | 233/1178 | 233/1178-04 |  |  | 70.9533 | 26 | 100% | Installed 07/10/20
Northumbrian Water | Smailes Lane CSO | 234/1158 |  |  |  | 77 | 35 | 99.7%
Northumbrian Water | Smith Street SPS | 235/1652 | 235/1652-01 |  |  | 15.5 | 4 | 99.97%
Northumbrian Water | Smith's Dock Road SPS | QC.25/04/1590 | S1 |  |  | 0 | 0 | 100%
Northumbrian Water | Smith's Dock Road SPS & CSO | 25/04/1599 |  |  |  | 0 | 0 | 99.93%
Northumbrian Water | Smithy Lane CSO | 235/1558 |  |  |  | 0 | 0 | 94.4%
Northumbrian Water | Snowdon Road SPS | QR.25/04/1511 | A |  |  | 166.9139 | 37 | 100% | Point changed to logger from install on 28/10/20.
Northumbrian Water | Snows Green Road CSO | 234/1165 |  |  |  | 3 | 1 | 88.77% | Comms. failure 17/10/20-26/11/20. First visit on 28/10/20 hadn't rectified the issue.
Northumbrian Water | Soft Leas SPS | QC.25/05/5020 | A1 |  |  | 410.3175 | 41 | 100%
Northumbrian Water | Solingen Estate CSO | EPRAB3090EN |  |  | Blyth South Beach | 0.33333 | 1 | 99.76%
Northumbrian Water | South Benwell Road CSO | 235/1958 |  |  |  | 17.8769 | 23 | 99.79%
Northumbrian Water | South Blyth Harbour CSO | 226/1210 |  |  | Blyth South Beach | 91.7333 | 23 | 99.72%
Northumbrian Water | South Church CSO | EPRBB3494EG |  |  |  | 0 | 0 | 87.89% | Comms. failed 14/11/20-end of year. Was visited on 18/11/20 however comms. weren't restored on old unit so stock of new logger required for install.
Northumbrian Water | South Cleatlam CSO | Permit Anomaly |  |  |  | 4 | 3 | 98.51% | Reported as 252/C/0147 in 2019 return. Permit anomaly to be corrected.
Northumbrian Water | South East View CSO (EA075) | 255/1214 |  |  |  | 4.75 | 10 | 99.99%
Northumbrian Water | South End SPS | Permit Anomaly |  |  |  | 1.1667 | 3 | 99.99% | Permit anomaly to be corrected.
Northumbrian Water | South Farm CSO | 244/0941 |  |  |  | 0.75 | 2 | 91.82%
Northumbrian Water | South Green Lane SPS | 225/0962 | A1 |  |  | 0.066944 | 1 | 100%
Northumbrian Water | South Moor Memorial Park CSO | 245/1179 |  |  |  | 292.25 | 29 | 99.62%
Northumbrian Water | South Moor Road Football Club CSO | 245/1262 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | South of Cockfield STW CSO | 242/1058 |  |  |  | 1.25 | 1 | 75.24% | Believe signal issues affected three local CSOs in Cockfield in July 2020. Cellos couldn't be restored to full comms. so Point Blues were installed, but due to technical comms. issues, the communications aren't robust. Comms. failed 07/07/20-13/07/20, 19/08/20-27/08/20, 10/09/20-05/10/20, 13/10/20-09/11/20,03/12/20-09/12/20 & 28/12/20-end of year.
Northumbrian Water | South of Rookwood CSO | 226/1268 |  |  |  | 3.5 | 7 | 82.08% | Comms. failed 19/04/20-28/04/20 and 04/08/20-06/08/20. Due to corruption only sending partial data transfers 29/08/20-28/09/20.
Northumbrian Water | South Park CSO | 25/03/1230 |  |  |  | 148.5 | 38 | 99.99%
Northumbrian Water | South Park East CSO (Ref Dl007) | 253/1280 |  |  |  | 1 | 4 | 99.99%
Northumbrian Water | South Road No 18 CSO | NPSWQD006905 |  |  |  | 0.5 | 1 | 95.75%
Northumbrian Water | South Road Weir CSO (Scotts Park) (WOOLER CSO) | 210/D/0271 |  |  |  | 0 | 0 | 92.62%
Northumbrian Water | South Shields Interceptor CSO No BS_104 | 235/B/0170 |  |  |  | 535.3394 | 70 | 100%
Northumbrian Water | South Shore Rd (East) | 235/1658 | 235/1658-01 |  |  | 81.5508 | 27 | 100%
Northumbrian Water | South Shore Road CSO | 235/1661 |  |  |  | 55.9333 | 41 | 99.67%
Northumbrian Water | South Street CSO | 244/0919 |  |  |  | 0 | 0 | 88.79% | Since install of new unit poor data have been received, dropping operability figure as this has been removed. The data don't suggest the unit was in spill at these times however.
Northumbrian Water | South Street CSO (ST003) | 254/1825 |  |  |  | 5 | 5 | 99.85%
Northumbrian Water | South Terrace CSO | 234/1147 |  |  |  | 14 | 4 | 99.99%
Northumbrian Water | South View CSO | 25/01/0915 |  |  |  | 0 | 0 | 72.11% | Regularly suffers from water ingress and connection between sensor and logger becomes corrupt. Therefore the logger sends no data back, but dials in. Difficult to identify these issues, and problem is persistent. Issue from 28/03/20-03/04/20, 18/04/20-29/04/20. Comms. then failed 29/05/20-20/08/20. As problem hasn’t been resolved this requires a Point Blue install, however due to delays in getting these to communicate with SCADA, this site isn’t operable.
Northumbrian Water | South Wylam SPS | 233/1039 | 233/1039-01 |  |  | 62 | 39 | 69.4% | Comms. failed 11/01/20-21/01/20 and 01/09/20-10/12/20.
Northumbrian Water | Southfield CSO | NPSWQD002462 |  |  | Seahouses North | 0.73333 | 3 | 99.99%
Northumbrian Water | Southfield Road CSO | 235/1507 |  |  |  | 0.25 | 1 | 78.14% | Comms. failure since 03/10/20. Estates issues as livestock have now entered the field and boundaries have changed preventing access.
Northumbrian Water | Southfields CSO | 245/1280 |  |  |  | 15.5 | 9 | 99.98%
Northumbrian Water | Sowerby Crescent/North Road Junction CSO | 25/04/1570 |  |  |  | 44.25 | 4 | 99.99%
Northumbrian Water | Spillars SPS | 235/1760 | 235/1760-01 |  |  | 573.9347 | 71 | 100%
Northumbrian Water | Spittal Quay CSO (BT7) | 210/1360 |  |  | Spittal | 71.6667 | 36 | 99.99%
Northumbrian Water | Spring Court CSO (Dl006) | 253/1275 |  |  |  | 20.25 | 7 | 89.54% | Water ingress between sensor and logger caused corruption. Therefore the logger sends no data back, but dials in. Difficult to identify these issues, and problem is persistent. Unable to visit to begin with as confined space entry approval needed due to COVID-19. Issue from 05/04/20-13/05/20.
Northumbrian Water | Spring Field Cottages CSO | 233/1243 |  |  |  | 0.25 | 1 | 99.87%
Northumbrian Water | Spring Way CSO (ST021) | 254/1827 |  |  |  | 26.5 | 28 | 99.21%
Northumbrian Water | Springwell Park CSO | 235/1704 |  |  |  | 115.75 | 24 | 91.99%
Northumbrian Water | SPS at Junc. Western Road/Rosehill Road | 235/1521 | 235/1521-01 |  |  |  |  | 0% | Unmonitored at present. Scheduled to be installed.
Northumbrian Water | St Aidens Park CSO | 232/1011 |  |  |  | 0 | 0 | 99.85%
Northumbrian Water | St Andrews Road CSO | 235/1715 |  |  |  | 52.75 | 26 | 98%
Northumbrian Water | St Germain's Lane CSO | 25/06/1017 |  |  | Marske | 18 | 19 | 99.99%
Northumbrian Water | St Helens Lane CSO | 233/1090 |  |  |  | 17 | 18 | 99.99%
Northumbrian Water | St Helens Street CSO | 233/1245 |  |  |  | 0.25 | 1 | 98.98%
Northumbrian Water | St Ives Road CSO (DER035) | 234/1140 |  |  |  | 0 | 0 | 97.13%
Northumbrian Water | St James Church CSO | 225/1073 |  |  |  | 3.25 | 1 | 99.96%
Northumbrian Water | St Lawrence Court Warkworth Sewerage System CSO MH | 223/B/0057 |  |  | Warkworth & Amble Links | 0.3 | 1 | 99.99%
Northumbrian Water | St Leonard's Rd CSO (L92) | 25/06/0998 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | St Lukes Road CSO (SU062) | 245/1372 | [5 empty] | 0% | Unmonitored at present. Highlighted on the change control form.
Northumbrian Water | St Mary's Primary School CSO | 234/1173 |  |  |  | 121.25 | 33 | 86.72% | Comms. failed 14/11/20-end of year. Was visited on 20/11/20 but contractor were unable to rectify comms. on old logger, and required stock before they were able to install new logger.
Northumbrian Water | St Mary's SPS | EPRBB3597VK | A1 |  |  | 453.1611 | 35 | 100% | Point changed to logger from install on 13/01/21.
Northumbrian Water | St Nicholas Hospital CSO | 235/1548 |  |  |  | 1 | 2 | 88.38% | Regularly suffers from water ingress and connection between sensor and logger becomes corrupt. Therefore the logger sends no data back, but dials in. Difficult to identify these issues, and problem is persistent. Issue between 16/09/20-28/09/20, 05/10/20-07/10/20 & 13/10/20-05/11/20.
Northumbrian Water | St. Aidans SPS | 221/1073 | 221/1073-01 |  | Seahouses North | 0.36667 | 1 | 96.93%
Northumbrian Water | Stags Head CSO | 244/1015 |  |  |  | 60.75 | 30 | 99.94%
Northumbrian Water | Staigs Garth SPS | 222/0853 | 222/0853-01 |  |  | 0 | 0 | 99.77%
Northumbrian Water | Staindrop SPS | 252/1020 | A |  |  | 254.5 | 55 | 93.53%
Northumbrian Water | Staindrop STW | 25/02/1109 | 25/02/1109-03 |  |  |  |  | 0% | Monitor present, although data is not to our reporting standard and an investigation in place to address matter.
Northumbrian Water | Stainsby Road CSO | 254/1816 |  |  |  | 22 | 9 | 99.99%
Northumbrian Water | Stainton CSO | 252/1052 |  |  |  | 15 | 9 | 99.98%
Northumbrian Water | Stamfordham CSO | 226/G/0092 |  |  |  | 9.25 | 19 | 99.99%
Northumbrian Water | Stamfordham Road SPS | 235/1394 | 235/1394-01 |  |  | 15.1303 | 3 | 100%
Northumbrian Water | Stamfordham STW | 226/A/0875 |  |  |  | 309.9428 | 52 | 100%
Northumbrian Water | Stanghow Road No.2 CSO | 25/06/1025 |  |  |  | 169.25 | 51 | 99.97%
Northumbrian Water | Stanhope Close CSO (SU26) | 245/1356 |  |  |  | 76.5 | 40 | 99.9%
Northumbrian Water | Stanhope STW | 241/1100 | 241/1100-03 |  |  | 922.4197 | 72 | 99.99%
Northumbrian Water | Stanhope Swimming Pool CSO | EPRBP3729GJ |  |  |  | 126.25 | 47 | 98.24%
Northumbrian Water | Stannington Village SPS | 226/1000 | A1 |  |  | 604.2003 | 43 | 99.98%
Northumbrian Water | Stapleton SPS | 252/D/0167 | A1 |  |  | 1.9347 | 2 | 99.97%
Northumbrian Water | Startforth SPS | 252/0992 | A |  |  | 90.1192 | 18 | 100% | Point upgraded from 25/11/20.
Northumbrian Water | Station Bank CSO | 233/1024 |  |  |  | 70.25 | 40 | 96.78%
Northumbrian Water | Station Bank CSO (DU021) | 245/1296 |  |  |  | 17.5 | 21 | 99.21%
Northumbrian Water | Station Hotel SPS & CSO | 256/1078 | A1 (Storm sewage) |  |  | 108 | 29 | 99.97%
Northumbrian Water | Station House SPS Bardon Mill | 232/0989 | 232/0989-01 |  |  | 59.3542 | 18 | 99.9%
Northumbrian Water | Station Lane CSO (CH011) | 245/1313 |  |  |  | 1.25 | 4 | 90.82%
Northumbrian Water | Station Road CSO | 233/1253 |  |  |  | 39 | 7 | 99.73%
Northumbrian Water | Station Road CSO | 235/1702 |  |  |  | 328.5 | 46 | 99.95%
Northumbrian Water | Station Road CSO | 245/1284 |  |  |  | 90.8 | 58 | 96.93%
Northumbrian Water | Station Road CSO | 254/1809 |  |  |  | 105 | 29 | 96.8%
Northumbrian Water | Station Road CSO | 255/1221 |  |  |  | 31.75 | 29 | 99.86%
Northumbrian Water | Station Road CSO | 256/1067 |  |  | Redcar Coatham | 9.5 | 12 | 99.98%
Northumbrian Water | Station Road CSO (G020) | 234/1127 |  |  |  | 35.25 | 27 | 99.58%
Northumbrian Water | Station Villas SRT CSO | 235/1709 |  |  |  | 0 | 0 | 99.86%
Northumbrian Water | Stella Road CSO | 233/1225 |  |  |  | 0.25 | 1 | 99.97%
Northumbrian Water | Stephenson St SPS | 235/1689 | 235/1689-01 |  |  | 108.5 | 39 | 99.97%
Northumbrian Water | Stephenson Way SPS | 25/03/1243 |  |  |  | 46.7264 | 11 | 99.99%
Northumbrian Water | Steppey Lane CSO (A020) | 222/0860 |  |  |  | 1.1667 | 5 | 98.07%
Northumbrian Water | Stepping Stones CSO | 223/0949 |  |  |  | 88 | 26 | 99.46%
Northumbrian Water | Steppy Lane SPS | 222/0868 | 222/0868-01 |  |  | 14.8464 | 9 | 100%
Northumbrian Water | Stillington Old Works CSO (ST004) | 254/1844 |  |  |  | 37.5 | 24 | 99.96%
Northumbrian Water | Stobs Ford SPS | 225/G/0400 | A1 |  |  | 254.8778 | 62 | 100%
Northumbrian Water | Stockton Road CSO | 254/1820 |  |  |  | 20 | 19 | 99.66%
Northumbrian Water | Stokesley SPS No 1 CSO | 254/C/0427 |  |  |  | 1.2483 | 2 | 99.3% | Installed 21/10/20. Logged until 17/07/20, comms. failed and revisited ley 10/09/20.
Northumbrian Water | Stokesley SPS No 2 CSO | 254/C/0428 | A1 |  |  | 159.5236 | 30 | 99.99%
Northumbrian Water | Stokesley STW | 25/04/1656 | A3 |  |  | 242.9261 | 21 | 82.51% | Installed 08/04/20. Logger not yet commissioned hence unvalidated data and due to communication issues low operability.
Northumbrian Water | Stonebridge SPS | 244/0491 | [5 empty] | 0% | Unmonitored at present. Scheduled to be installed.
Northumbrian Water | Stonebridge SPS | 244/0491 | A1 |  |  | 85.75 | 41 | 99.91%
Northumbrian Water | Stoney Lane CSO | 235/1928 |  |  |  | 1.75 | 5 | 99.99%
Northumbrian Water | Stoney Rigg CSO | 232/1178 |  |  |  | 0.25 | 1 | 99.99%
Northumbrian Water | Stoney Row CSO | 235/1532 |  |  |  | 18.75 | 17 | 99.73%
Northumbrian Water | Storey Park CSO | 225/1077 |  |  |  | 0 | 0 | 98.54% | Data provided for additional site not identified on the EDM Tracker as requested by REDACTED letter dated 08/02/21.
Northumbrian Water | Stotfield Burn CSO | 241/1050 |  |  |  | 28.75 | 13 | 15.72% | Operability <90% due to poor comms. - The monitor requires a site visit to download the data as it's situated in a remote location with poor network coverage and no electricity supply.
Northumbrian Water | Straight Lane CSO (Dl023) | 254/1806 |  |  |  | 40 | 17 | 99.93%
Northumbrian Water | Strait Lane (Strawberry Cottage SPS) Dl023 | Permit Anomaly |  |  |  | 123.75 | 29 | 99.43% | This was incorrectly reported in 2019 return as 254/1806 Hurworth Place CSO. Permit anomaly to be corrected.
Northumbrian Water | Stressholme STW | 25/04/1797 | 25/04/1797-04 |  |  |  |  | 0% | Unmonitored at present. Scheduled to be installed.
Northumbrian Water | Summerhill CSO | 233/1227 |  |  |  | 0 | 0 | 100%
Northumbrian Water | Sun Inn CSO | 225/1059 |  |  |  | 5.25 | 5 | 97.07%
Northumbrian Water | Sunderland Bridge CSO | 243/D/0368 |  |  |  | 107 | 49 | 99.53%
Northumbrian Water | Sunderland Bridge STW | 243/0976 | 243/0976-04 |  |  | 670.8378 | 29 | 100% | Point upgraded from 16/11/20.
Northumbrian Water | Sunderland CSO Barley Mow Park | EPR/CB3191AV |  |  |  | 0 | 0 | 99.99% | Data provided for additional site not identified on the EDM Tracker as requested by REDACTED letter dated 08/02/21.
Northumbrian Water | Sunderland Road CSO | 255/1222 |  |  |  | 9.5 | 17 | 95.95%
Northumbrian Water | Sundial Place CSO | 25/04/1604 |  |  |  | 15.75 | 11 | 99.95%
Northumbrian Water | Sunniside CSO G103 | EPRBB3498WT |  |  |  | 0 | 0 | 92.36%
Northumbrian Water | Sunnybrow SPS | 243/D/0395 | A1 |  |  | 607.25 | 77 | 99.59%
Northumbrian Water | Swaddles Hole CSO (NC061) | 235/1915 |  |  |  | 0 | 0 | 98.8%
Northumbrian Water | Swainby STW - Storm Tank | 254/1962 | 254/1962-03 |  |  |  |  | 0% | Monitor present, although data is not to our reporting standard and an investigation in place to address matter.
Northumbrian Water | Swarland Fence SPS | 223/0839 | A |  |  | 462.8275 | 72 | 99.99%
Northumbrian Water | Swarland Old STW CSO | 223/0947 |  |  |  | 56.25 | 20 | 99.86%
Northumbrian Water | Swinburn Street CSO (was Oakwellgate (South End)) | 235/1925 |  |  |  | 133.2711 | 69 | 99.98%
Northumbrian Water | Swinburne Place CSO | 235/1967 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Tame Bridge SPS | 25/04/1692 | 25/04/1692-01 |  |  | 136.25 | 17 | 93.91%
Northumbrian Water | Tanfield Comprehensive School CSO | 235/1716 |  |  |  | 1 | 3 | 99.89%
Northumbrian Water | Tanfield Trunk Sewer CSO (DER050) | 235/1931 |  |  |  | 35.75 | 16 | 97.76%
Northumbrian Water | Tanners Road CSO (TD028) | 233/1238 |  |  |  | 1.5333 | 5 | 99.99%
Northumbrian Water | Tanton Rd CSO (HM13) | 25/04/1629 |  |  |  | 0 | 0 | 99.69%
Northumbrian Water | Tay Street CSO | 234/1160 |  |  |  | 4 | 7 | 99.99%
Northumbrian Water | Taylor Street CSO | 226/1050 |  |  |  | 79.75 | 32 | 95.93%
Northumbrian Water | Teams CSO | EPRBB3893EZ |  |  |  | 126.1978 | 112 | 83.18% | Old CSO provided monitoring until 09/11/20. After this time logger in temporary CSO provided data. Being managed by capital investment project. Comms. failed in this period (01/12/20-01/01/21).
Northumbrian Water | Tedder Avenue CSO | 254/E/0431 |  |  |  | 2.75 | 6 | 98.74%
Northumbrian Water | Tees Dock Road CSO (L009) | 254/1935 |  |  |  | 79 | 21 | 80.34% | H&S access issue with ORA. Narrow entry to chamber so specific RAMS needed to access. Comms. failed 27/05/20-24/06/20, 24/08/20-01/09/20.
Northumbrian Water | Teesbank Avenue CSO | 254/0663 |  |  |  | 124.0333 | 45 | 99.99%
Northumbrian Water | Teesdale Avenue CSO | 254/1836 |  |  |  | 31.5 | 15 | 99.99%
Northumbrian Water | Teesside High School SPS | QC.25/04/1431 | A |  |  |  |  | 0% | Monitor present, although data is not to our reporting standard and an investigation in place to address matter.
Northumbrian Water | Temple House SPS | 232/1141 | 232/1141-01 |  |  | 473.25 | 50 | 99.41%
Northumbrian Water | Temple Street CSO (STY066) | 235/1943 |  |  |  | 160.2461 | 51 | 100%
Northumbrian Water | Ten Acre Farm CSO (NTY064) | 226/1251 |  |  |  | 4.75 | 2 | 99.72%
Northumbrian Water | The Black Swan CSO | 25/02/1100 |  |  |  | 4 | 6 | 61.69% | Intermittent comms. at this location. Comms. failed 19/05/20-27/05/20. Spurious data received 29/06/20-16/07/20 reducing operability. Out of comms. again 17/09/20-02/11/20 when a Point Blue was installed, but comms. still not being received. Traffic management is required to visit this site so there is a slow turnaround.
Northumbrian Water | The Boathouse SPS | 235/1729 | 235/1729-01 |  |  | 0.063333 | 1 | 99.99% | Point changed to logger from install on 02/12/20.
Northumbrian Water | The Brooms North CSO | 235/1843 |  |  |  | 0.25 | 1 | 93.68%
Northumbrian Water | The Caravan Park CSO | 232/1153 |  |  |  | 323 | 101 | 98.94%
Northumbrian Water | The Carrs Tilery Lane CSO | 25/06/1027 |  |  |  | 0 | 0 | 64.35% | Newly installed monitor with poor comms. since install (17/09/20) and when comms. were working backfill of data frequently poor.
Northumbrian Water | The Fallows CSO | 242/1063 |  |  |  | 0 | 0 | 73.98% | Believe signal issues affected three local CSOs in Cockfield in July 2020. Cellos couldn't be restored to full comms. so Point Blues were installed, but due to technical comms. issues, the communications aren't robust and unit is transmitting intermittent data packets, so some data are missing from transmission, reducing operability.
Northumbrian Water | The Firs CSO | 232/1167 |  |  |  | 4 | 3 | 99.86%
Northumbrian Water | The Gable CSO | 224/0955 |  |  |  | 1.5 | 3 | 99.99%
Northumbrian Water | The Green CSO | 25/04/1605 |  |  |  | 0 | 0 | 97.14%
Northumbrian Water | The Green Market CSO | 235/1484 |  |  |  | 177.5 | 57 | 99.97%
Northumbrian Water | The Hagg CSO | 251/0862 |  |  |  | 177.6 | 40 | 84.69% | Comms. failed 06/11/20-end of year. Attempted to resolve on 16/11/20 however Cello couldn't be repaired and unavailability of Point Blue stock due to technical issues surrounding new tender have resulted in poor operability for this site.
Northumbrian Water | The Hollow CSO | 241/1108 |  |  |  | 71 | 29 | 99.99%
Northumbrian Water | The Hollows CSO (WV50) | 241/1125 |  |  |  | 279.25 | 59 | 89.85% | Comms. failed 30/11/20-end of year. Site visited on 10/12/20 however crew had to abort due to high levels in sewer due to rainfall.
Northumbrian Water | The Lendings (Startforth) SPS & CSO | 252/0993 | A (Storm Sewage) |  |  | 116.5 | 27 | 99.65%
Northumbrian Water | The Meadows CSO | 254/1819 |  |  |  | 6 | 8 | 97.71%
Northumbrian Water | The Meadows CSO (CH78) | 245/1329 |  |  |  | 12.3625 | 9 | 99.97%
Northumbrian Water | The Middles CSO | 245/1148 |  |  |  | 177.4328 | 75 | 99.99% | Set to 2 minutes to resolve data spikes.
Northumbrian Water | The New Road CSO | 25/04/1711 |  |  |  | 1.75 | 2 | 98.79%
Northumbrian Water | The Old School CSO | 25/01/0916 |  |  |  | 0.25 | 1 | 99.99%
Northumbrian Water | The Oval CSO | 235/1839 |  |  |  | 1 | 4 | 99.99%
Northumbrian Water | The Oval SPS | 235/1764 | 235/1764-01 |  |  | 0 | 0 | 99.98%
Northumbrian Water | The Peth CSO | 232/1013 |  |  |  | 0 | 0 | 96.75%
Northumbrian Water | The Slack (No 24) | 242/1064 |  |  |  | 3.6667 | 5 | 14.51% | Operability <90% due to poor comms. - The monitor requires a site visit to download the data as it's situated in a remote location with poor network coverage and no electricity supply.
Northumbrian Water | The Slack CSO | 242/1069 |  |  |  | 24.6667 | 8 | 16.62% | Operability <90% due to poor comms. - The monitor requires a site visit to download the data as it's situated in a remote location with poor network coverage and no electricity supply.
Northumbrian Water | The Stray Storm Sewage Retention Tank | 25/06/1016 |  |  | Marske | 24.3333 | 5 | 99.98%
Northumbrian Water | The Swirle CSO | 235/1918 |  |  |  | 99.6089 | 48 | 100%
Northumbrian Water | The Vicarage CSO | 232/1140 |  |  |  | 264.25 | 53 | 97.83%
Northumbrian Water | The Yarker Lane CSO (Ref.TE71) | 25/01/0917 |  |  |  | 37 | 19 | 99.58%
Northumbrian Water | Thornton Street CSO | 25/04/1769 |  |  |  | 9.25 | 9 | 98.18%
Northumbrian Water | Thorpe Street SPS | QC.25/05/5022 | A1 |  |  | 899.205 | 86 | 100%
Northumbrian Water | Thorpe Thewles SPS | 254/0974 | A1 |  |  | 129.6208 | 28 | 99.97%
Northumbrian Water | Thropton & Snitter STW | 223/0943 | A2 |  |  | 317.5481 | 32 | 100% | Point changed to logger from install on 02/11/20.
Northumbrian Water | Thropton SPS | 223/0980 | A1 |  |  | 20.3997 | 2 | 94.94% | Installed 30/10/20
Northumbrian Water | Throstles Nest CSO | 255/1192 |  |  |  | 0 | 0 | 93.9%
Northumbrian Water | Throstles Nest SPS | 255/1203 | 255/1203-01 |  |  | 0 | 0 | 99.96%
Northumbrian Water | Tilery Farm Storage Tank CSO | 255/1185 |  |  |  | 258.5 | 47 | 99.92%
Northumbrian Water | Tilery Storm SPS | 254/1822 |  |  |  | 489.9572 | 71 | 100% | Point changed to logger from install on 24/11/20.
Northumbrian Water | Tindale STW | 232/1147 | 232/1147-02 |  |  | 123.5206 | 24 | 99.79%
Northumbrian Water | Toad Pool CSO (TE351) | 242/1049 |  |  |  | 6 | 6 | 99.98%
Northumbrian Water | Toft Hill Ejector Station CSO & EO | 242/1050 | 242/1050-01 |  |  | 121.5 | 31 | 99.38%
Northumbrian Water | Togston STW | 224/0992 | 224/0992-03 |  |  | 278.1547 | 70 | 100%
Northumbrian Water | Toll House Road CSO | 244/1001 |  |  |  | 76 | 50 | 98.84%
Northumbrian Water | Tollesby Lane CSO | 25/04/1665 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Tollesby Manor SPS & CSO | 254/1894 | A |  |  | 0 | 0 | 99.17%
Northumbrian Water | Tool Hire CSO (Ref.DU042) | 244/0996 |  |  |  | 87.5 | 35 | 99.46%
Northumbrian Water | Tow Law STW - CSO Inlet | 241/1106 | 241/1106-04 |  |  | 253.25 | 64 | 97.41%
Northumbrian Water | Tow Law STW - Storm Tank | 241/1106 | 241/1106-03 |  |  | 188.9753 | 80 | 99.87%
Northumbrian Water | Tower Street CSO - M2 Monitoring Point | 25/04/1700 | A2 |  |  | 7.1 | 9 | 99.99% | EDM1
Northumbrian Water | Tower Street CSO - M4 Monitoring Point | 25/04/1700 | A1 |  |  | 0 | 0 | 99.44%
Northumbrian Water | Travellers Green CSO (SE015) | 253/1263 |  |  |  | 108.75 | 57 | 99.7%
Northumbrian Water | Trimdon Colliery SPS | 25/03/1233 | A1 |  |  | 239.8047 | 51 | 100%
Northumbrian Water | Trimdon Village STW - CSO Inlet | 25/03/1232 | 25/03/1232-03 |  |  |  |  | 0% | Unmonitored at present. Scheduled to be installed.
Northumbrian Water | Trimdon Village STW - Storm Tank | 25/03/1232 | 25/03/1232-02 |  |  | 526.4556 | 54 | 99.98%
Northumbrian Water | Tuart Street CSO (NO1) | Permit Anomaly |  |  |  | 0 | 0 | 99.98% | Permit anomaly to be corrected.
Northumbrian Water | Tudhoe Mill STW - CSO Inlet | 243/0985 | A3 |  |  | 171.1403 | 46 | 100%
Northumbrian Water | Tudhoe Mill STW - Storm Tank | 243/0985 | A2 |  |  | 479.445 | 63 | 100%
Northumbrian Water | Tudor Croft Cottage CSO | 256/1043 |  |  |  | 145.75 | 32 | 99.35%
Northumbrian Water | Tudor Road CSO (STY068) | 235/1905 |  |  |  | 90.5833 | 26 | 99.91%
Northumbrian Water | Tunberry Way CSO | 235/1964 |  |  |  | 0 | 0 | 98.85%
Northumbrian Water | Turner Street CSO | 223/0950 |  |  | Warkworth & Amble Links | 71.1 | 39 | 99.97% | EDM1
Northumbrian Water | Tuthill Stairs CSO | 235/1922 |  |  |  | 0.75 | 2 | 77.64% | Many spurious data points removed between 22/02/20-12/05/20. Spurious data rectified on visit this day.
Northumbrian Water | Tweedside Industrial Estate CSO | 210/1335 |  |  | Spittal | 16 | 19 | 99.99%
Northumbrian Water | Tyne Green CSO | 233/1239 |  |  |  | 2.4667 | 9 | 99.99%
Northumbrian Water | Tyne Street SPS | 235/1656 | 235/1656-01 |  |  | 0 | 0 | 99.99%
Northumbrian Water | Tyne View CSO | 233/0991 |  |  |  | 107.4 | 52 | 99.99%
Northumbrian Water | Tyne View SPS | 235/1690 | 235/1690-01 |  |  | 9.6878 | 17 | 100%
Northumbrian Water | Tyneside CSO - Newland Drive | 235/B/0169 |  |  |  | 289.73 | 39 | 100%
Northumbrian Water | Tyneside CSO - South Extraction Building | 235/B/0168 |  |  |  | 133.5033 | 36 | 100%
Northumbrian Water | Ulgham STW | 224/A/0887 |  |  |  | 786.13/2.26 | 49/5 | 100%/100% | Multiple meters on tanks for a single discharge activity. Investigation into a single meter to be conducted.
Northumbrian Water | Ullswater Crescent CSO (WV056) | 241/1130 |  |  |  | 121 | 38 | 99.99%
Northumbrian Water | Union Quay CSO | EPRBB3497EZ |  |  |  | 1.2667 | 2 | 91.62%
Northumbrian Water | Ushaw Moor (Joyce Terrace & Deerness View) STW | 244/E/0315 | 244/E/0315-01 |  |  | 396.1697 | 28 | 100% | Full year spill data provided but as Historic logging began on 07/08/2020 operability prior to this is unknown.
Northumbrian Water | Usworth Hall CSO | 235/1953 |  |  |  | 0.25 | 1 | 99.09%
Northumbrian Water | Valley Terrace CSO (WV046) | 241/1122 |  |  |  | 69.5 | 23 | 94.94%
Northumbrian Water | Vedra Close CSO | 241/A/0999 |  |  |  | 22 | 5 | 93.29%
Northumbrian Water | Veronica Street CSO | 254/1205 |  |  |  | 106.5 | 31 | 99.95%
Northumbrian Water | Victoria Embankment-Polam Lane CSO | 25/03/1231 |  |  |  | 48.75 | 13 | 99.97%
Northumbrian Water | Victoria Road at Sandown Gardens CSO | 235/1933 |  |  |  | 58.6667 | 28 | 97.8%
Northumbrian Water | Victoria Road SPS | 25/03/1253 | 25/03/1253-02 |  |  | 2.7372 | 5 | 100%
Northumbrian Water | Vindomora Villas CSO | 234/1155 |  |  |  | 17 | 15 | 99.99%
Northumbrian Water | Vinovium CSO A27 | 242/C/0385 |  |  |  | 28.5 | 25 | 99.99%
Northumbrian Water | Vinovium CSO No A13 | 242/C/0371 |  |  |  | 9.25 | 9 | 99.99%
Northumbrian Water | Vinovium CSO No A14 | 242/C/0372 |  |  |  | 3.5 | 10 | 99.74%
Northumbrian Water | Vinovium CSO No A17 | 242/C/0375 |  |  |  | 5.5 | 10 | 99.99%
Northumbrian Water | Vinovium CSO No A22 | 242/C/0380 |  |  |  | 0 | 0 | 82.8% | Comms. failed 29/10/20-end of year. Was visited on 04/11/20 however customer didn't leave gates open for access despite being contacted. Revisited 11/11/20 however logger sent no data back, but dialled in. Released for install of new unit, but not completed by contractor.
Northumbrian Water | Vinovium CSO No A9 | 242/C/0368 |  |  |  | 0.25 | 1 | 99.99%
Northumbrian Water | Vinovium STW | 243/0966 | 243/0966-03 |  |  | 592.4003 | 47 | 99.93%
Northumbrian Water | Vivian Avenue SU013 | 245/1375 |  |  |  | 34.75 | 24 | 97.76%
Northumbrian Water | Vulcan Street SPS | QR.25/04/1513 | A |  |  |  |  | 0% | Unmonitored at present. Scheduled to be installed.
Northumbrian Water | Waddington Street CSO | 245/1287 |  |  |  | 0 | 0 | 98.93%
Northumbrian Water | Wades Farm CSO (WV010) | 242/1061 |  |  |  | 22 | 14 | 99.89%
Northumbrian Water | Wagonway Road SPS | 235/1745 | 235/1745-01 |  |  | 1951.5061 | 142 | 100%
Northumbrian Water | Waldridge Road CSO (CH13) | 245/1305 |  |  |  | 0.25 | 1 | 99.98%
Northumbrian Water | Walkergate Durham CSO | EPRCB3097WP |  |  |  | 72 | 30 | 96.61%
Northumbrian Water | Wallridge STW | Permit Anomaly |  |  |  | 107.7328 | 38 | 96.94% | Installed 07/04/20
Northumbrian Water | Wansbeck Road CSO | 226/1256 |  |  |  | 0 | 0 | 99.98%
Northumbrian Water | Wapping Street CSO | 235/1902 |  |  |  | 89.5 | 25 | 92.17%
Northumbrian Water | Warden Grove CSO | 245/C/0293 |  |  |  | 69.25 | 44 | 99.94%
Northumbrian Water | Warden Village STW CSO | 231/0271 | 231/0271-03 |  |  | 0.75 | 2 | 99.99%
Northumbrian Water | Wark On Tweed SPS | 210/1312 | 210/1312-03 |  |  | 44.5 | 21 | 99.51%
Northumbrian Water | Wark STW | 231/1071 | 231/1071-03 |  |  | 47.6622 | 12 | 100% | Point upgraded from 26/11/20.
Northumbrian Water | Warrenby SPS | 256/0908 | A |  | Redcar Coatham | 0 | 0 | 100%
Northumbrian Water | Warsdell Street SPS | 226/1154 | 226/1154-01 |  |  | 3.75 | 6 | 99.99%
Northumbrian Water | Washington STW - CSO Inlet | 245/1244 | 245/1244-04 |  |  |  |  | 0% | Monitor installed 31/03/20 but not commissioned. Investigation to address the matter required.
Northumbrian Water | Washington STW - Storm Tank | 245/1244 | 245/1244-03 |  |  |  |  | 0% | Unmonitored in 2020. Installed 16/02/21 in acceptance phase.
Northumbrian Water | Washington Village Cemetery CSO | NPSWQD006113 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Washingwell School CSO | 235/1508 |  |  |  | 0.25 | 1 | 73.42% | Comms. failed 29/04/20, however contractor were unable to lift lid on visit. Eventually when lid was unseized the next visit resulted in failed comms. afterwards. Due to issues with Point Blues dialling into SCADA no adequate replacement until 27/08/20.
Northumbrian Water | Waterhouses CSO | EPRAB3691VY |  |  |  | 74.25 | 8 | 99%
Northumbrian Water | Waterville Road CSO | 235/1898 |  |  |  | 0.46667 | 3 | 99.99%
Northumbrian Water | Watts Slope High Level CSO (A56) | 235/1796 |  |  | Whitley Bay | 0 | 0 | 99.86%
Northumbrian Water | Wear Chare (Batts Terrace) CSO | 241/1116 |  |  |  | 90.5 | 53 | 99.51%
Northumbrian Water | Wear View A CSO | 243/0992 |  |  |  | 1.75 | 6 | 99.98%
Northumbrian Water | Wear View B CSO | 243/0921 |  |  |  | 7.75 | 2 | 98.99%
Northumbrian Water | Well Bank CSO | 233/1252 |  |  |  | 171.75 | 58 | 99.22%
Northumbrian Water | Well Bank CSO | 25/03/1254 |  |  |  | 6.5 | 7 | 99.99%
Northumbrian Water | Wellfield SPS | 255/1108 | 255/1108-02 |  |  | 47.25 | 10 | 99.81%
Northumbrian Water | Wellington Lane SPS | 245/1211 | 245/1211-01 |  |  | 34.75 | 19 | 98.72%
Northumbrian Water | Welwyn Factory CSO | 226/1267 |  |  |  | 49.25 | 28 | 99.39%
Northumbrian Water | Wesley Terrace CSO | 235/1536 |  |  |  | 11.25 | 4 | 99.99%
Northumbrian Water | West Boldon CSO (No 3) | 235/F/0613 |  |  |  | 0 | 0 | 92.47%
Northumbrian Water | West Boldon CSO (No 4) | 235/F/0614 |  |  |  | 378.5 | 84 | 99.91%
Northumbrian Water | West Cornforth SPS | 243/0979 | A1 |  |  | 29.5 | 15 | 99.35%
Northumbrian Water | West End SPS | 25/04/1596 | A1 |  |  | 149.9089 | 23 | 99.86%
Northumbrian Water | West Holborne South CSO | 235/1945 |  |  |  | 25.25 | 12 | 99.65%
Northumbrian Water | West Of Hedworth Lane CSO STY03 | 235/C/0044 |  |  |  | 27.5 | 25 | 99.8%
Northumbrian Water | West Rainon STW Manhole No 21 CSO | 245/E/0505 |  |  |  | 1 | 3 | 99.53%
Northumbrian Water | West Rainton CSO (DU081) | 245/E/0506 |  |  |  | 23 | 24 | 99.03%
Northumbrian Water | West Rainton CSO (DU085) | 245/E/0507 |  |  |  | 54.75 | 35 | 99.91%
Northumbrian Water | West Road CSO (WV63) | 241/1138 |  |  |  | 220.25 | 51 | 99.83%
Northumbrian Water | West Row CSO (HP008) | 254/1810 |  |  |  | 13.75 | 16 | 99.77%
Northumbrian Water | West Sleekburn Farm CSO | 226/1048 |  |  |  | 128.25 | 17 | 99.2%
Northumbrian Water | West St CSO | 243/0914 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | West Street SPS CSO | 254/E/0336 |  |  |  | 32.5708 | 9 | 100%
Northumbrian Water | West View CSO | 235/1317 |  |  |  | 2.9667 | 9 | 99.99%
Northumbrian Water | West View Road CSO | 255/1116 |  |  |  | 6.25 | 10 | 99.99%
Northumbrian Water | West Woodburn CSO | 255/1186 |  |  |  | 11.25 | 8 | 99.31%
Northumbrian Water | West Woodburn SPS | 231/0966 | 231/0966-01 |  |  | 25.6089 | 8 | 95.87%
Northumbrian Water | Westbourne Drive CSO | 245/1366 |  |  |  | 9.25 | 11 | 99.98%
Northumbrian Water | Western Area STW | 241/1146 | 241/1146-02 |  |  | 703.3142 | 73 | 98.97%
Northumbrian Water | Westfield Court CSO | 254/1921 |  |  |  | 5.5 | 7 | 98.6%
Northumbrian Water | Westfield No9 SPS | 210/0983 | 210/0983-02 |  |  | 67 | 7 | 99.45%
Northumbrian Water | Westgate Caravan Site CSO | 241/1064 |  |  |  | 22.5 | 5 | 88.89% | Spurious data being intermittently since March, reducing operability. H&S issue accessing raised manhole chamber means this hasn't been resolved.
Northumbrian Water | Westgate CSO | 241/E/0471 |  |  |  | 56 | 18 | 81.38% | Spurious data received from PTI during February 2020-16/03/20. Occurred again from 25/08/20-08/09/20, further reducing operability. Comms also failed 02/11/20-19/11/20.
Northumbrian Water | Westline Industrial Estate CSO | 235/1872 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Whalton STW | 226/0927 | B |  |  | 84.0625 | 22 | 99.25% | Installed 07/04/20
Northumbrian Water | Whessoe SPS | 253/0053 |  |  |  | 26.8819 | 6 | 100%
Northumbrian Water | Whickham CSO Sunniside Road Grange Lane | 235/1966 |  |  |  | 0.25 | 1 | 99.99%
Northumbrian Water | Whiskey Jacks SPS | 234/1174 | 234/1174-02 |  |  | 105.7406 | 32 | 98.31% | Point changed to logger from install on 27/10/20.
Northumbrian Water | Whitburn CSO | 245/1106 |  |  | Seaburn (Whitburn North) | 0 | 0 | 99.99%
Northumbrian Water | Whitburn Steel SPS | 245/1207 | 245/1207-01 |  | Seaburn (Whitburn North) | 67.9178 | 23 | 100%
Northumbrian Water | White St/Station Road CSO | 235/1329 |  |  |  | 247.6183 | 59 | 100% | This site is currently under investigation, and a worse case scenario has been reported. These discharges are most likely to be in system spills (bifurcation).
Northumbrian Water | White St/Station Road CSO | 235/1330 |  |  |  | 65.6953 | 48 | 100% | This site is currently under investigation, and a worse case scenario has been reported. These discharges are most likely to be in system spills (bifurcation).
Northumbrian Water | Whitehouse Road CSO | 254/1823 | 254/1823-1.3.1 |  |  | 2.75 | 2 | 99.99%
Northumbrian Water | Whitehouse Road CSO | 254/1823 | 254/1823-1.3.2 |  |  | 22 | 27 | 99.8%
Northumbrian Water | White-Le-Head Allotments CSO | 235/1539 |  |  |  | 0 | 0 | 99.98%
Northumbrian Water | Whittingham STW | 222/0864 | 222/0864-04 |  |  | 232.5158 | 18 | 100%
Northumbrian Water | Whittle Colliery Village STW | 223/0832 | [5 empty] | 0% | Unmonitored at present. Scheduled to be installed.
Northumbrian Water | Whorlton STW | 25/02/1087 | 25/02/1087-03 |  |  | 455.6719 | 27 | 100% | Point changed to logger from install on 26/11/20.
Northumbrian Water | Widdrington CSO | 224/0995 |  |  |  | 0.7 | 2 | 97.71%
Northumbrian Water | William Street CSO | 235/1746 |  |  |  | 2.75 | 6 | 99.99%
Northumbrian Water | William Street CSO | 245/1266 |  |  |  | 0.5 | 2 | 99.99%
Northumbrian Water | Willington CSO | 243/D/0393 |  |  |  | 71.25 | 37 | 99.93%
Northumbrian Water | Willington STW | 243/0968 | 243/0968-03 |  |  | 235.1992 | 26 | 100% | Installed 16/04/20
Northumbrian Water | Willow Bridge CSO | 226/1239 |  |  |  | 24.25 | 18 | 77.5% | Comms failed on 20/09/20-14/12/20. REDACTED TEXT. Instruction passed on how to access the chamber safely.
Northumbrian Water | Wincomblee B SPS | 235/1757 | Sch 1/3 |  |  | 1.7561 | 3 | 99.99% | Point changed to logger from install on 19/11/20.
Northumbrian Water | Wincomblee C SPS | 235/1758 |  |  |  | 62.5 | 24 | 99.99% | Didn’t report in 2019 return. Monitor present, although data is not to our reporting standard and an investigation in place to address matter.
Northumbrian Water | Wincomblee Road CSO | 235/1759 | [5 empty] | 0% | Monitor present, although data is not to our reporting standard and an investigation in place to address matter.
Northumbrian Water | Windlestone STW | 253/1269 |  |  |  | 451.81/811.12/448.30 | 47/58/37 | 100%/100%/100% | Multiple meters for a single discharge activity. Investigation into a single meter to be conducted.
Northumbrian Water | Windmill Cottage (The Mill) CSO (TE066) | 252/1125 |  |  |  | 29.6667 | 15 | 77.08% | Comms. failed 09/10/20-end of year. Attempted to resolve on 30/10/20 however due to a road closure the site was inaccessible. A further visit on 18/11/20 was aborted REDACTED TEXT. Accessed on 17/12/20 however Cello couldn't be repaired and unavailability of Point Blue stock due to technical issues surrounding new tender meant issue wasn't resolved.
Northumbrian Water | Wingate CSO No 1 | 255/E/0642 |  |  |  | 1.25 | 5 | 99.99%
Northumbrian Water | Winston STW - CSO Inlet | 25/02/1104 | 25/02/1104-01 |  |  | 0 | 0 | 99.99%
Northumbrian Water | Witton Gilbert CSO | 244/0889 |  |  |  | 216.75 | 65 | 99.12%
Northumbrian Water | Witton Gilbert STW | 244/1027 | 244/1027-02 |  |  | 262.7014 | 20 | 9.836% | Data prior to 26/11/20 inaccurate. Point upgraded and accurate from then.
Northumbrian Water | Wood Grove CSO (NC029) | 235/1939 |  |  |  | 71.6667 | 45 | 92.14%
Northumbrian Water | Woodborough Lane CSO | 25/04/1607 |  |  |  | 24.75 | 6 | 99.99%
Northumbrian Water | Woodfield Hill Crook CSO | EPRBB3499RX |  |  |  | 4.75 | 5 | 92.06%
Northumbrian Water | Woodford No22 CSO | 235/1520 |  |  |  | 15.25 | 31 | 95.63%
Northumbrian Water | Woodgate Gardens CSO | 235/1981 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Woodhouse Lane Library CSO | EPRBB3093WE |  |  |  | 2.25 | 8 | 99.99%
Northumbrian Water | Woodland View CSO | 255/1184 |  |  |  | 4.5 | 5 | 99.64%
Northumbrian Water | Woodlands Pumping Station No 3, Warkworth | 223/B/0223 | A1 |  | Warkworth & Amble Links | 5.9333 | 2 | 99.17%
Northumbrian Water | Woodlands SPS | 233/1065 | A |  |  | 101.0514 | 24 | 99.42% | Point changed to logger from install on 27/10/20.
Northumbrian Water | Woodwynd CSO | 235/A/0508 |  |  |  | 2.25 | 4 | 99.83%
Northumbrian Water | Wooler SPS | 210/0970 | A |  |  | 12.3336 | 11 | 99.99%
Northumbrian Water | Wooler STW | 210/1275 | A2 |  |  | 164.1167 | 34 | 98.56% | Point changed to logger from install on 08/06/20. Possible over reported data provided prior to this new install.
Northumbrian Water | Woolsington CSO | EPRCB3191ED |  |  |  | 0 | 0 | 93.65%
Northumbrian Water | Working Men's Club CSO | 243/1004 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Works CSO the Village Brancepeth | EPRBB3990WL |  |  |  | 0.25 | 1 | 95.19%
Northumbrian Water | Wormhill Terrace CSO | 245/1303 |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Worsall Road SPS CSO & EO (ST076) | 25/04/1648 | 25/04/1648-01 |  |  | 83.8153 | 14 | 100%
Northumbrian Water | Yarm Bridge CSO | 254/1178 |  |  |  | 2.75 | 7 | 99.88%
Northumbrian Water | Yarm Road CSO (Y2) | EPRMB3892EJ |  |  |  | 1.5 | 6 | 99.77%
Northumbrian Water | Yarm Road CSO (Y3) | EPRMB3892RF |  |  |  | 21.5 | 22 | 90.56%
Northumbrian Water | Yarm Road CSO (Y6) | EPRMB3892VE |  |  |  | 0 | 0 | 99.99%
Northumbrian Water | Yarm Road/Muirfield Road CSO | EPRCB3195EM |  |  |  | 0 | 0 | 98.85%
Northumbrian Water | York Hill SPS (SE034) | 243/1010 | 243/1010-02 |  |  | 0.53611 | 1 | 100% | Point changed to logger from install on 20/10/20.
Northumbrian Water | Zetland Row CSO | 256/1076 |  |  |  | 72 | 15 | 99.77%