## USER GUIDE - SO
EDM Storm Overflow Annual Return: Quick User Guide
!! See separate User Guide in Word format for further detail !!
General Guidance:
- The EDM annual return 2021 should list all storm overflows with spills to the environment (permitted/unpermitted with permit application made), irrespective of whether they are currently have EDM installed or existing EDM permit condition.
- The EDM annual return 2021 should include data for (1) All storm overflows with an existing EDM permit condition, and (2) All storm overflows with EDM intalled through the WINEP/AMP7 EDM programme, with or without a current EDM permit condition. Data should also be included for overflows where a permit has been applied for by the WaSC but not yet issued.
- WaSCs are expected to provide EDM data for overflows without a current EDM requirement (e.g. not secured through the WINEP nor with a permit requirement), where they deem this data accurate & representative of spills
- Reported spill data (count & duration) should be considered reliable, verified and an accurate representation of the spills that occurred during the reporting period. Data that is known to be erroneous should not be reported on. See main User Guide (Word document) for more information and examples.
- Base information (e.g. EA permit reference, site name, Outlet NGR etc.) on overflows must directly match the Environment Agency (EA) Consents Database (see "Resources" below).
- Where EDM reporting operability is <90% (Column Q) subsequent columns Primary Reason (Column R) and Action Taken / Planned (Column S) must be completed.
- If spill count data (column P + valid data in previous years) exceeds thresholds in the SOAF guidance then columns T, U, V (Spill Frequency - operational & planning info) must be completed.
- A number of columns are "do once"; the data are not expected to change year on year. These headings are highlighted in grey below. Data in remaining columns are expected to change each year. These headings are highlighted in light green below.
- Water Framework Directive (WFD) data in columns I & J have been pre-populated by the EA using the Outlet NGR provided by WaSCs [November 2021] in column H.
- Any additional overflows not previously provided, or newly-reconciled Consents Database permit references must be submitted by WaSCs to the EA by Friday 21 January 2022. The EA will then identify the relevant WFD information & return to WaSCs on Friday 28 January ahead of final submission by WaSCs the following month.
Resources:
- Environment Agency national consents database: |  | Consented Discharges to Controlled Waters with Conditions - data.gov.uk
(Note the EA Consents Database is updated quarterly on .gov.uk)
- Environment Agency Risk-Based Approach to the Monitoring of Storm Discharges (September 2013)
- Environment Agency Storm Overflow Assessment Framework (June 2018): |  |  | Storm Overflow Assessment Framework
Guide to columns & drop-down selection:
Water Company Name | (Column A)
Site Name (EA Consents Database) | (Column B)
- Site name that matches exactly with column "Discharge_Site_Name" on EA consents database
Site Name (WaSC Operational Name) | (Column C)
- Site name used by the WaSC for operational reasons. The EA Consents Database Site Name must be provided in column B - the WaSC site name is not a substitute
- Column C is optional
EA Consents Database Permit Reference | (Column D)
- As shown in column "Permit Number" on EA Consents Database. NB: this may occassionally differ from number shown on actual permit or WaSC URN/folio
WaSC Supplementary Permit Ref. | (Column E)
- WaSC reference number for permitted overflow. The EA Consents Database permit reference must be provided in column D - the WaSC permit reference is not a substitute
- Column E is optional
Activity reference | (Column F)
- Listed on new format permits under Schedule 1 – “Operations” (e.g. A1 / A2 etc.)
- Listed on old format permits under Schedule conditions (e.g. Schedule No. A.115K/00-01)
- NB: This is not the same as columns “DISCHARGE_SITE_TYPE_CODE” or “DSI_TYPE_DESCRIPTION” on EA consents database
Storm discharge asset type | (Column G)
- As detailed in risk-based approach to EDM document (2013)
- See the more detailed User Guide (Word format) for a table of definitions (page 6)
- NB: This is not the same as columns “DISCHARGE_SITE_TYPE_CODE” or “DSI_TYPE_DESCRIPTION” on EA consents database
Drop-down options Column G:
SO on sewer network | On network - storm overflow. Can be direct or associated with a network storm tank. Not associated with pumping station
Storm discharge at pumping station | On network - pumping station
Inlet SO at WwTW | Storm overflow (direct to the environment) permitted as part of a WwTW permit. Exception is a storm tank - see note on next row
Storm tank at WwTW | Storm overflow via a storm tank, permitted as part of a WwTW permit. Note this can be physically remote from the WwTW
Other storm discharge asset type | Any storm overflow that does not clearly align with the four categories above. These may be used to devlop future drop-down categories.
Outlet discharge NGR (Consents Database) | (Column H)
- This is the actual discharge point to the environment.
- Listed on EA consents database as “OUTLET_GRID_REF”. This is the reference to use
- Also listed on new format permits under Schedule 3 - "Discharge Point NGR"
- Also listed on old format permits under "Place of Discharge"
- NB: This is not the same as columns “DISCHARGE_NGR” (discarhge site NGR) or “EFFLUENT_GRID_REF” (effluent monitoring NGR) on EA consents database
WFD Waterbody ID (Cycle 2) | (Column I)
- Identification number of WFD waterbody at the discharge point (as per Cycle 2)
- Prefixed with "GB…"
- Pre-populated by EA using outlet discharge NGR (column H). Any further overflows requiring the EA to populate WFD information must be submitted to the EA by Friday 21 January 2022
WFD Waterbody Catchment Name (Cycle 2) | (Column J)
- Name of WFD waterbody catchment at the discharge point (as per Cycle 2)
- NB: This is not the same as "CATC_NAME" on EA consents database
- Pre-populated by EA using outlet discharge NGR (column H). Any further overflows requiring the EA to populate WFD information must be submitted to the EA by Friday 21 January 2022
Receiving Water / Environment - common name (Consents Database) | (Column K)
- Listed on EA consents database under "RECEIVING_WATER" NB: this may differ from receiving water shown on actual permit
- Also listed on new format permits under Schedule 3 - "Discharge Point"
- Also listed on old format permits under "Place of Discharge"
Shellfishery | (Column L)
- Populate for storm overflows that have Shellfish Water EDM requirements
Bathing Beach | (Column M)
- Populate for storm overflows that have Bathing Water EDM requirements
Initial EDM commission date | (Column N)
- Date EDM commissioned; the date data can be expected from the EDM
- See the more detailed User Guide (Word format) for more detailed table of definitions (page 7)
- Note: Installation date may precede commissioned date
Drop-down options Column M:
Installed but not yet commissioned | Installed in current reporting year but data not yet expected
Commissioned in 2020 - full year data expected | Installed in previous reporting year
Commissioned in 2019 - full year data expected | Installed in previous reporting year
Commissioned in 2018 - full year data expected | Installed in previous reporting year
Commissioned in 2017 - full year data expected | Installed in previous reporting year
Commissioned in 2016 - full year data expected | Installed in previous reporting year
Commissioned pre-2016 - full year data expected | Installed in previous reporting year
Jan 2021
Feb 2021
Mar 2021
April 2021
May 2021
June 2021
July 2021
August 2021
September 2021
October 2021
November 2021
December 2021
EDM to be installed by December 2023 | EDM not yet installed
Total Duration (hr) of all spills | (Column O)
- Total spill duration prior to processing through the 12-24h count method
Counted spills using 12-24h count method | (Column P)
- Spill count post-processed through the 12-24h count method
EDM Operation - % reporting period EDM operational | (Column Q)
- Based on Initial Commissioning Date (Column M) e.g. commissioned in July of reporting year then period Jul-Dec would be 100%; if commissioned in previous reporting year then period Jan-Dec would be 100%
- e.g. commissioned in September of reporting year then 100% reporting period would be Sep.-Dec.
- e.g. commissioned in any previous reporting year then 100% reporting period would be Jan.-Dec.
- See the more detailed User Guide (Word format) for further information & examples
EDM Operation - Reporting % - Primary Reason <90% | (Column R)
- Core reason why EDM may not have been operational <90% of period (Column Q)
- Select primary reason only
- Category must be selected when period of EDM operation (column Q) is less than 90%. Optional to complete this column when period of EDM operation is 90% or over
- See the more detailed User Guide (Word format) for table of definitions (page 8)
Drop-down options Column R:
Access - Unable to retrieve data from non-telemetry data logger (NB: not to be used for delayed access to fix existing fault) | When access causes inability to retrieve data; e.g. landowner permission. Consider core reason – if caused by poor installation or design then select “Installation set-up/design issue” category instead. Not to be used for delayed access t fix existing operational fault
Capital / maintenance works affect EDM operation | Where planned works affect EDM operation. Consider core reason – if caused by poor installation or design then select “Installation set-up/design issue” category instead
Comms failure / issue | Any part of communication failure; e.g. intermittent signal or antenna damage. Consider core reason – if caused by poor installation or design then select “Installation set-up/design issue” category instead. Similar if comms loss caused by power failure – select “Power failure / issue” instead
EDM not yet installed | E.g. not yet scheduled for installation, or installation not currently feasible
EDM installed - not yet commissioned | E.g. installed after reporting period. E.g. installed within reporting period but data not yet calibrated
Installation set-up/design issue | When installation or design (e.g. choice of location) affects EDM operability. E.g. Original design location cannot distinguish between two overflows & original EDM needs to be relocated to more representative point. E.g. Original design location affected by river ingress & EDM requires relocation. E.g. Alternative monitor type required
Power failure / issue | Any part of power failure; e.g. loss of mains supply / battery fault. Consider core reason – if caused by cutting through cable then select “Capital / maintenance works” category instead
Sensor failure / issue | Any part of sensor failure; e.g. water ingress to connection between sensor & logger. Consider core reason – if water ingress caused by poor choice of location for installation & requires adjustment then select “Installation set-up/design issue” category instead
Telemetry or data archiving failure / issue | Any part of telemetry failure; e.g. dial-in or storage/sending of data problems. Consider core reason – if archiving problem caused by power fault or incorrect installation then use “Power failure / issue” or ”Installation set-up/design issue” categories respectively. Similar if data transfer caused by intermittent signal – select “Comms failure / issue” instead
No longer operational as an overflow - permit revoked or to be revoked
Reporting % - Action taken / planned - Status & Timeframe | (Column S)
- Indicate whether action has already been taken / is planned to be taken, or whether there is an ongoing investigation to identify the appropriate action
- Which month this activity was completed / is planned
- See the more detailed User Guide (Word format) for table of definitions (page 10)
Drop-down options Column R:
Scheduled | Appropriate operational action to address <90% EDM operation is planned
Resolved - January | Appropriate operational action has already been taken & issue affecting EDM operation resolved
Resolved - Feburary | As above
Resolved - March | As above
Resolved - April | As above
Resolved - May | As above
Resolved - June | As above
Resolved - July | As above
Resolved - August | As above
Resolved - September | As above
Resolved - October | As above
Resolved - November | As above
Resolved - December | As above
N/A - Ongoing investigation | Appropriate action not yet identified
N/A - EDM to be installed by December 2023 | Use when selection in Column R is “EDM not yet installed”
Spill Frequency - Operational Review Outcome - Primary Reason | (Column T)
- Core reason for spill count (Column P)
- Select primary reason only
- Category must be selected when spill frequency exceeds SOAF threshold (using column P + data from previous years)
- See the more detailed User Guide (Word format) for table of definitions (page 10)
Drop-down options Column T:
Performance - Partial / no capacity due to blockage or restriction (e.g. roots / grid) - maintenance issue | Spill frequency primarily caused by maintenance issue; e.g. roots causing channel restriction e.g. blocked screens causing premature spills
Performance - Sewer collapse (partial / full) - infrastructure issue | Spill frequency primarily caused by infrastructure issue; e.g. partial collapse of sewer
Performance - Groundwater inundation | Groundwater inundation is primary reason for spills; e.g. GW inundation in chalk catchment causing high spill frequency
Performance - Infiltration | High spill frequency caused by infiltration. Requires investment to infrastructure to resolve
Performance - Asset power failure | E.g. frequent power supply failure caused high spill frequency
Performance - Pump failure / issue | Spill frequency primarily caused by pump failure / premature spills; e.g. pumping station struggles to maintain PFF & review of rising main design required
Performance - Other maintenance / capital works (e.g. jetting) | Spill frequency primarily caused by works; e.g. jetting
Performance - Not designed to meet Bathing / Shellfish Water directive | Spill frequency threshold reached because asset not yet designed to meet BW or SFW requirements
Performance - Asset configuration (e.g. PS/rising main/storm tanks) | Spill frequency primarily caused by inappropriate asset/configuration; e.g. inlet design causing premature spills & requires further investigation
Data collection - EDM non-representative location | E.g. Records multiple discharge points & cannot distinguish between the two. Requires relocation
Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | High spill frequency caused by exceptional weather events. Subsequent analysis of these data show adjusted spill frequency now not above SOAF threshold
Data collection - Tidal / river inundation | EDM spill frequency data quality affected by tidal or river inundation; e.g. tidal cycle causes levels to reverse flows in outfall pipe
Data collection - Poor quality (e.g. logger calibration / sensor issues) | E.g. logger calibration / sensor issues
Not asset maintenance - hydraulic capacity | Spill frequency primarily caused by hydraulic capacity issue rather than something that can be fixed operationally
Spill Frequency - Action taken / planned - Status & Timeframe | (Column U)
- Indicate whether action has already been taken / is planned to be taken, or whether there is an ongoing investigation to identify the appropriate action
- Which month this activity was completed / is planned
- Category must be selected when spill frequency exceeds SOAF threshold (using column P + data from previous years)
- See the more detailed User Guide (Word format) for table of definitions (page 11)
Drop-down options Column U:
Scheduled | Appropriate operational action to address spill frequency is planned
Resolved - January | Appropriate operational action has already been taken & issue affecting spill frequency resolved
Resolved - Feburary | As above
Resolved - March | As above
Resolved - April | As above
Resolved - May | As above
Resolved - June | As above
Resolved - July | As above
Resolved - August | As above
Resolved - September | As above
Resolved - October | As above
Resolved - November | As above
Resolved - December | As above
N/A - Ongoing investigation | Appropriate operational action not yet identified
N/A - Hydraulic Capacity | Issue is due to hydraulic capacity and unable to be fixed operationally through asset maintenance programme
Spill Frequency - Planning review position | (Column V)
- Action taken to address spill performance through the planning framework
- Select primary reason only
- Category must be selected when spill frequency exceeds SOAF threshold (using column O + data from previous years)
- Follows SOAF for addressing high frequency discharges from storm overflows under the UWWTR (see Figure 1 in SOAF document, 2018)
- Stage 1 of the SOAF should be applied to all high spills as good practice, as part of the initial investigation to understand whether spills were due to exceptional weather events, asset performance or hydraulic capacity. Stage 1 is expected on a continual rolling basis independent of any WINEP drivers.
- Progressing further past stage 1 is expected when a WINEP driver exists. Progressing past stage 1 without a WINEP driver would be proactive but at WaSC discretion.
- See the more detailed User Guide (Word format) for table of definitions (page 12)
Drop-down options Column V:
SOAF N/A - Proposed SFTP (overflow previously improved) | Schemes previously improved via SOAF but now identified for Spill Frequency Trigger Permitting
Stage 1a: Confirmed "exceptional weather" issue | See SOAF definition
Stage 1b: Confirmed "asset maintenance" issue | See SOAF definition
Stage 1c: Confirmed "hydraulic issue" | If not “exceptional weather” or “asset maintenance”
U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | SOAF invesitgation ongoing at Stage 2/3
U_INV driver - Stage 4: Cost beneficial outcome not yet determined | In process of Cost Benefit Analysis (CBA) but no outcome at present
U_INV driver - Stage 4: No cost beneficial solution | CBA indicates costs are disproportionate to environmental benefit
U_IMP4 driver - Stage 4: Spill reduction scheme - On current WINEP/AMP7 or Green Recovery | U_INV CBA indicates spill reduction scheme is cost beneficial and is on current WINEP or other planned improvement programme
U_IMP4 driver - Stage 4: Potential spill reduction scheme - Not yet on current WINEP/AMP7 or Green Recovery | U_INV CBA indicates a spill reduction scheme may be cost beneficial
N/A - Operational solution applied | Planning framework not required - spill frequency remedied through operational solution

## NWL - SO
EDM STORM OVERFLOW REGULATORY ANNUAL RETURN
Please send to email inbox: askED@environment-agency.gov.uk
Please name file using the following convention: "EDM Return WaSC period.xls" .
For example if Severn Trent Water had a bathing water return for 2021 it would be "EDM Return Severn Trent Water Bathing Season 2021.xls"
For example if Wessex Water had a storm overflow annual return for 2021 it would be "EDM Return Wessex Water Storm Overflow Annual 2021.xls"
For example if Southern Water had an emergency overflow annual return for 2021 it would be "EDM Return Southern Water Emergency Overflow Annual 2021.xls"
Red text - Requires attention (e.g. permit number not found on Consents Database)
Pink text - amended by EA - please review (e.g. reference amended to match Consents Database)
Cell is missing data - to be completed by WaSC | [16 empty] | Complete columns R & S when data in column Q is <90% |  | Enter in columns T, U, V when relevant spill frequency data (column P + valid historic) is above the SOAF threshold (pg. 2 of SOAF)
Blue text = populated by EA (using WaSC information provided Nov 2021/Jan 2022)
Water Company Name | Site Name (EA Consents Database) | Site Name (WaSC operational) [optional] | EA Permit Reference (EA Consents Database) | WaSC Supplementary Permit Ref. [optional] | Activity Reference on Permit (if >1 discharge on permit) | Storm Discharge Asset Type | Outlet Discharge NGR (EA Consents Database) | WFD Waterbody ID (Cycle 2) (discharge outlet) | WFD Waterbody Catchment Name (Cycle 2) (discharge outlet) | Receiving Water / Environment (common name) (EA Consents Database) | Shellfish Water (only populate for storm overflow with a Shellfish Water EDM requirement) | Bathing Water (only populate for storm overflow with a Bathing Water EDM requirement) | Initial EDM Commission Date | Total Duration (hrs) all spills prior to processing through 12-24h count method | Counted spills using 12-24h count method | EDM Operation - % of reporting period EDM operational | EDM Operation - Reporting % - Primary Reason <90% | EDM Operation - Action taken / planned - Status & timeframe | High Spill Frequency - Operational Review - Primary Reason | High Spill Frequency - Action taken / planned - Status & timeframe | High Spill Frequency - Environmental Enhancement - Planning Position (Hydraulic capacity)
Northumbrian Water | NORTH ROAD NO1 | 6NW801451 | 235/1505 | 235/1505 |  | SO on sewer network | NZ3543062360 | GB103023075690 | Don from Source to Tidal Limit | DON |  |  | Commissioned pre-2016 - full year data expected | 3 | 2 | 99.7%
Northumbrian Water | 223 GENEVA ROAD CSO | 6NW801356(1) | #TBC | Permit Anomaly | To be permitted for storm | SO on sewer network | NZ3069012933 | GB103025072160 | Neasham Stell Catchment (trib of Tees) | Cree Beck into Kent Beck |  |  | Commissioned pre-2016 - full year data expected | 3.75 | 3 | 99.81%
Northumbrian Water | CSO 28 BEWESHILL CRESCENT | 6NW801056 | 233/1082 | 233/1082 |  | SO on sewer network | NZ1685262360 | GB103023074791 | Blaydon Burn | BLAYDON BURN |  |  | Commissioned pre-2016 - full year data expected | 1.9333 | 4 | 97.98%
Northumbrian Water | 29/30 NORTH ROAD CSO | 6NW801452 | #TBC | Permit Anomaly | To be permitted for storm | SO on sewer network | NZ3543562357 | GB103023075690 | Don from Source to Tidal Limit | River Don |  |  | Commissioned pre-2016 - full year data expected | 1.75 | 2 | 90.54%
Northumbrian Water | 33 DOCK ROAD CSO | 6NW800830 | 210/1345 | 210/1345 |  | SO on sewer network | NT9973552213 | GB510202110000 | TWEED | RIVER TWEED (SALINE ESTUARY) |  | Spittal | Commissioned pre-2016 - full year data expected | 123.0003 | 49 | 96.34%
Northumbrian Water | BURNSIDE AVENUE CSO | 6NW801428 | 245/1318 | 245/1318 |  | SO on sewer network | NZ3292050300 | GB103024077580 | Lumley Park Burn from Source to Herrington Burn | MOORS BURN TRIBUTARY |  |  | Commissioned pre-2016 - full year data expected | 0.5 | 1 | 99.99%
Northumbrian Water | 50 WOODSIDE GARDENS CSO | 6NW801112 | 245/1309 | 245/1309 |  | SO on sewer network | NZ2095551570 | GB103024077590 | Twizell Burn from Source to Cong Burn | STANLEY BURN TRIB |  |  | Commissioned pre-2016 - full year data expected | 78.75 | 22 | 99.97%
Northumbrian Water | 66 ROSS LEA CSO | 6NW801411 | 245/1370 | 245/1370 |  | SO on sewer network | NZ3235051888 | GB103024077630 | Herrington Burn from Source to Lumley Park Burn | HERRINGTON BURN |  |  | Commissioned pre-2016 - full year data expected | 90.75 | 31 | 99.39%
Northumbrian Water | A1068 ROAD BRIDGE CSO | 6NW800868 | 223/0871 | 223/0871 |  | SO on sewer network | NU2483206265 | GB510302203000 | COQUET | COQUET ESTUARY |  | Warkworth & Amble Links | Commissioned pre-2016 - full year data expected | 33.1667 | 24 | 94.31%
Northumbrian Water | A66 RIDER SEWER CSO | 6NW801559 | 254/0937 | 254/0937 |  | SO on sewer network | NZ4678718620 | GB510302509900 | Tees | OLD RIVER TEES |  |  | Commissioned pre-2016 - full year data expected | 11.75 | 14 | 99.99%
Northumbrian Water | A690 SLIP ROAD CSO, SU27 | 6NW801427 | 245/1357 | 245/1357 |  | SO on sewer network | NZ3345049090 | GB103024077580 | Lumley Park Burn from Source to Herrington Burn | RAINTON BURN |  |  | Commissioned pre-2016 - full year data expected | 20.5 | 11 | 99.99%
Northumbrian Water | A692 CSO | 6NW800940 | 234/1117 | 234/1117 |  | SO on sewer network | NZ0850049000 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | DENE BURN |  |  | Commissioned pre-2016 - full year data expected | 7.5 | 14 | 99.67%
Northumbrian Water | ABATTOIR ST CSO | 6NW801537 | 254/1860 | 254/1860 |  | SO on sewer network | NZ4312017250 | GB103025072550 | Lustrum Beck Catchment (trib of Tees) | TRIB OF HARTBURN BECK |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | ABBEY COURT (AMPLEFORTH AVENUE) CSO | 6NW801595 | 254/1855 | 254/1855 |  | SO on sewer network | NZ5475118719 | 10 | #N/A | CROSS BECK |  |  | Commissioned pre-2016 - full year data expected | 15 | 9 | 99.89%
Northumbrian Water | ACKLAM ROAD CSO | 6NW800424 | 25/04/1673 | 25/04/1673 | 25/04/1673-01 | SO on sewer network | NZ4614917663 | 10 | #N/A | THE OLD RIVER TEES |  |  | Commissioned in 2020 - full year data expected | 221.7361 | 194 | 100% |  |  | Data collection - EDM non-representative location
Northumbrian Water | ACKLAM STREET OUTFALL | 6NW800648 | QR.25/04/1512 | QR.25/04/1512 | A1 | Storm discharge at pumping station | NZ4956521392 | GB510302509900 | Tees | River Tees |  |  | Commissioned in 2020 - full year data expected | 38.2889 | 63 | 99.95%
Northumbrian Water | ACOMB CRESCENT (CATHEDRAL) CSO | 6NW801152 | 235/1609 | 235/1609 |  | SO on sewer network | NZ2296069880 | GB103023075780 | Ouse Burn from Source to Tyne | OUSE BURN |  |  | Commissioned pre-2016 - full year data expected | 27 | 14 | 99.91%
Northumbrian Water | ACOMB CSO | 6NW800893 | 233/G/0243 | 233/G/0243 |  | SO on sewer network | NY9264465247 | GB103023075801 | Tyne from Watersmeet to Tidal Limit | RIVER TYNE |  |  | Commissioned pre-2016 - full year data expected | 165.2336 | 79 | 99.66% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | ACOMB PUMPING STATION | 6NW800495 | 233/1041 | 233/1041 | 233/1041-01 | Storm discharge at pumping station | NY9306065460 | GB103023075730 | Red Burn (Trib of Tyne) | BIRKLEY BURN (RIVER TYNE) |  |  | Commissioned in 2020 - full year data expected | 222.1197 | 35 | 100%
Northumbrian Water | ADDERLANE SCHOOL CSO (TD035) | 6NW800960 | 233/1249 | 233/1249 |  | SO on sewer network | NZ1037263365 | GB103023075801 | Tyne from Watersmeet to Tidal Limit | ADDERLANE GILL TRIB PARK BURN |  |  | Commissioned pre-2016 - full year data expected | 26.8333 | 8 | 100%
Northumbrian Water | ADDISON VILLAGE CSO UNIT 3 | 6NW800246 | 233/1023 | 233/1023 |  | SO on sewer network | NZ1697664214 | GB510302310200 | TYNE | TYNE |  |  | Commissioned in 2020 - full year data expected | 15.415 | 12 | 100%
Northumbrian Water | AINSLEY STREET CSO | 6NW800323 | NPSWQD002839 | NPSWQD002839 |  | SO on sewer network | NZ2667042673 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | CLVRTD TRIB OF RIVER WEAR |  |  | Commissioned in 2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | AISLABY QUAY SPS | 6NW800615 | 254/1928 | 254/1928 | A1 | Storm discharge at pumping station | NZ4071712229 | GB103025072595 | Tees from Skerne to Tidal Limit | RIVER TEES |  |  | Commissioned pre-2016 - full year data expected | 59 | 8 | 99.94%
Northumbrian Water | ALBANY ROAD/SALTMEADOWS ROAD CSO | 6NW801243 | 235/1659 | 235/1659 |  | SO on sewer network | NZ2669063657 | GB510302310200 | TYNE | TYNE SALINE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 37.7 | 30 | 99.87%
Northumbrian Water | ALBION TERRACE STORM RETENTION | 6NW800433 | 255/1092 | 255/1092 |  | SO on sewer network | NZ5305733526 | GB650301500005 | Tees Coastal | NORTH SEA |  |  | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
Northumbrian Water | ALDBROUGH ST JOHN SEWAGE PUMPING | 6NW800743 | 25/02/1081 | 25/02/1081 | 25/02/1081-01 | Storm discharge at pumping station | NZ2059011050 | GB103025072060 | Aldbrough Beck from Forcett Park Catch to Clow Bk | ALDBROUGH BECK |  |  | Commissioned in 2020 - full year data expected | 1439.3481 | 77 | 100%
Northumbrian Water | ALDBROUGH SEWAGE TREATMENT WORKS | 6NW800742 | 25/02/1079 | 25/02/1079 | 25/02/1079-03 | Storm tank at WwTW | NZ2077010840 | GB103025072060 | Aldbrough Beck from Forcett Park Catch to Clow Bk | ALDBROUGH BECK |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | BEAR PARK (ALDIN GRANGE) STW | 6NW800757 | 244/0991 | 244/0991 | 244/0991-03 | Storm tank at WwTW | NZ2490043190 | GB103024077551 | Browney from Smallhope Burn Deerness confl | BROWNEY |  |  | Commissioned in 2020 - full year data expected | 893.2008 | 90 | 100%
Northumbrian Water | ALDIN GRANGE CSO | 6NW801180 | 244/1004 | 244/1004 |  | SO on sewer network | NZ2448543299 | GB103024077551 | Browney from Smallhope Burn Deerness confl | UNNAMED TRIB OF RIVER BROWNEY |  |  | Commissioned pre-2016 - full year data expected | 165 | 41 | 99.89%
Northumbrian Water | ALLENDALE STW | 6NW800700 | 232/1118 | 232/1118 | 232/1118-03 | Storm tank at WwTW | NY8281057030 | GB103023074710 | Allen from Source to West Allen | RIVER EAST ALLEN |  |  | Commissioned in 2020 - full year data expected | 2440.3169 | 124 | 100%
Northumbrian Water | ALLENSWAY CSO | 6NW800423 | 254/1382 | 254/1382 |  | SO on sewer network | NZ4634915842 | GB103025072180 | Stainsby Beck Catchment (trib of Tidal Tees) | STAINSBY BECK |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | ALN BANK CSO | 6NW800215 | 222/0865 | 222/0865 |  | SO on sewer network | NU0711612015 | GB103022076310 | Aln from Callaly Burn to Coe Burn | RIVER ALN |  |  | Mar 2021 | 0 | 0 | 99.58%
Northumbrian Water | ALNMOUTH ROAD SSO | 6NW800860 | 222/D/0255 | 222/D/0255 |  | SO on sewer network | NU1940013700 | GB103022076350 | Aln from Edlingham Burn to Tidal Limit | ALN |  |  | Commissioned pre-2016 - full year data expected | 110.75 | 41 | 97.97%
Northumbrian Water | ALNMOUTH P STATION | 6NW800476 | 222/0839 | 222/0839 | 222/0839-01 | Storm discharge at pumping station | NU2432010620 | GB510302203300 | ALN | RIVER ALN(SALINE ESTUARY) |  |  | Commissioned in 2019 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | ALNWICK CASTLE CSO A011 | 6NW800856 | 222/0857 | 222/0857 |  | SO on sewer network | NU1885113533 | GB103022076350 | Aln from Edlingham Burn to Tidal Limit | BOW BURN |  |  | Commissioned pre-2016 - full year data expected | 153.5 | 69 | 90.97% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | ALNWICK CASTLE CSO NO 2 A035 | 6NW800216 | 222/0827 | 222/0827 |  | SO on sewer network | NU1913913618 | GB103022076350 | Aln from Edlingham Burn to Tidal Limit | RIVER ALN |  |  | Commissioned in 2017 - full year data expected | 16.75 | 23 | 99.65%
Northumbrian Water | ALNWICK SEWAGE TREATMENT WORKS | 6NW800118 | 222/0862 | 222/0862 | A3 | Inlet SO at WwTW | NU2040013200 | GB103022076350 | Aln from Edlingham Burn to Tidal Limit | RIVER ALN |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | ALNWICK SEWAGE TREATMENT WORKS | 6NW800695 | 222/0862 | 222/0862 | A2 | Storm tank at WwTW | NU2040013200 | GB103022076350 | Aln from Edlingham Burn to Tidal Limit | RIVER ALN |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | Scheduled
Northumbrian Water | ALSTON EJECTOR STATION CSO | 6NW800877 | 232/1135 | 232/1135 | A1 | Storm discharge at pumping station | NY7161946248 | GB103023075531 | South Tyne from Black Burn to Tipalt Burn | RIVER SOUTH TYNE |  |  | Commissioned pre-2016 - full year data expected | 24.25 | 7 | 27.43% | Comms failure / issue | N/A - Ongoing investigation
Northumbrian Water | AMBLE HARBOUR PUMPING STATION | 6NW800482 | 223/0933 | 223/0933 | 223/0933-01 | Storm discharge at pumping station | NU2688004820 | GB510302203000 | COQUET | NORTH SEA |  | Warkworth & Amble Links | Commissioned in 2018 - full year data expected | 182.2783 | 39 | 100%
Northumbrian Water | AMBLE WASTE WATER TREATMENT WORKS | 6NW800122 | 223/0931 | 223/0931 | A2 | Inlet SO at WwTW | NU2767004990 | GB650301500001 | Northumberland South | NORTH SEA |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | AMELIA CLOSE CSO - C49/102 | 6NW800294 | 235/1316 | 235/1316 |  | SO on sewer network | NZ2207663278 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | Commissioned in 2018 - full year data expected | 15.7036 | 22 | 100%
Northumbrian Water | ANGATE STREET CSO | 6NW801629 | EPRBB3992AT | EPRBB3992AT |  | SO on sewer network | NZ0779937205 | GB103024077520 | Waskerley Beck from Source to Wear | WASKERLEY BECK |  |  | Commissioned pre-2016 - full year data expected | 0.75 | 2 | 92.21%
Northumbrian Water | ANICK CSO TD006 | 6NW800902 | 233/1242 | 233/1242 |  | SO on sewer network | NY9593265116 | GB103023075801 | Tyne from Watersmeet to Tidal Limit | UNNAMED TRIB RIVER TYNE |  |  | Commissioned pre-2016 - full year data expected | 304.75 | 37 | 98.01%
Northumbrian Water | HEXHAM (ANICK GRANGE) P.S. | 6NW800497 | 233/1046 | 233/1046 | 233/1046-01 | Storm discharge at pumping station | NY9480064970 | GB103023075801 | Tyne from Watersmeet to Tidal Limit | TYNE TRIB |  |  | Commissioned in 2020 - full year data expected | 169.3483 | 23 | 99.94%
Northumbrian Water | ANNFIELD PLAIN & STANLEY CSO 8 | 6NW800245 | EPRBB3491WR | EPRBB3491WR |  | SO on sewer network | NZ1670652607 | GB103023075670 | Team from Source to Tyne | CARRMYERS BURN |  |  | Commissioned in 2018 - full year data expected | 57 | 11 | 99.87%
Northumbrian Water | ANNITSFORD BRIDGE CSO | 6NW800335 | 226/1261 | 226/1261 |  | SO on sewer network | NZ2702273777 | GB103022076190 | Seaton Burn from Source to Tidal Limit | SEATON BURN |  |  | Commissioned in 2017 - full year data expected | 0 | 0 | 93.44%
Northumbrian Water | ARGYLE COURT CSO | 6NW801114 | EPRBP3427GC | EPRBP3427GC |  | SO on sewer network | NZ1967654170 | GB103023075670 | Team from Source to Tyne | Houghwell Burn |  |  | Commissioned pre-2016 - full year data expected | 1.25 | 1 | 96.44%
Northumbrian Water | ARMONSIDE RD CONNOLLY TERRACE CSO | 6NW800981 | 234/1124 | 234/1124 |  | SO on sewer network | NZ1287756827 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | RIVER DERWENT |  |  | Commissioned pre-2016 - full year data expected | 409.25 | 51 | 99.52% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | ASH MEADOWS CSO CHESTER LE STREET | 6NW801312 | 245/E/0593 | 245/E/0593 |  | SO on sewer network | NZ2829253005 | GB103024077624 | Wear DS of Lumley Park Burn to Tidal Limit | TRIB. OF WEAR ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 153.75 | 57 | 99.92% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | ASH TREE LANE CSO | 6NW801000 | 234/1056 | 234/1056 |  | SO on sewer network | NZ1425059540 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | SPEN BURN |  |  | Commissioned pre-2016 - full year data expected | 76.25 | 34 | 99.99%
Northumbrian Water | ASHINGTON CSO PARK ROAD WK 006 | 6NW801261 | 225/1029 | 225/1029 |  | SO on sewer network | NZ2708086616 | GB103022077062 | Wansbeck from Bothal Burn to North Sea | BLACKCLOSE BURN (R.WANSBECK) |  |  | Commissioned pre-2016 - full year data expected | 24.25 | 15 | 99.99%
Northumbrian Water | ASHINGTON DRIVE CSO HLF MOON RNDBWT | 6NW801259 | 225/0940 | 225/0940 |  | SO on sewer network | NZ2690486086 | GB103022077062 | Wansbeck from Bothal Burn to North Sea | WANSBECK ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 0.75 | 2 | 90.99%
Northumbrian Water | WESTBOURNE ESTATE SSO ASHKIRK WAY | 6NW801375 | 226/1274 | 226/1274 |  | SO on sewer network | NZ3073174473 | GB103022076190 | Seaton Burn from Source to Tidal Limit | SEATON BURN |  |  | Commissioned pre-2016 - full year data expected | 20 | 27 | 99.83%
Northumbrian Water | ASKRIGG STREET COMBINED SEWER OVERF | 6NW801332 | 253/1088 | 253/1088 |  | SO on sewer network | NZ2950016000 | GB103025072596 | Skerne from Demons Beck to Tees | RIVER SKERNE |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.71%
Northumbrian Water | ATHERSTONE DRIVE CSO (L022) | 6NW801611 | 256/1044 | 256/1044 |  | SO on sewer network | NZ6138915392 | GB103025071970 | Skelton Beck Catch (Saltburn) trib of North Sea | TRIBUTARY OF CHAPEL BECK |  |  | Commissioned pre-2016 - full year data expected | 34 | 9 | 98.96%
Northumbrian Water | ATHERTON STREET CSO | 6NW801229 | 245/1321 | 245/1321 |  | SO on sewer network | NZ2687642591 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | FLASS BURN |  |  | Commissioned pre-2016 - full year data expected | 0.75 | 2 | 99.61%
Northumbrian Water | ATKINSON ROAD CSO | 6NW800284 | 235/1315 | 235/1315 |  | SO on sewer network | NZ2160863384 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | Commissioned in 2018 - full year data expected | 22.63 | 26 | 100%
Northumbrian Water | ATTWOOD TERRACE CSO SE008 | 6NW801225 | 243/1002 | 243/1002 |  | SO on sewer network | NZ2654535606 | GB103024077464 | Wear from Gaunless to Browney | NICKY NACK BECK |  |  | Commissioned pre-2016 - full year data expected | 2.75 | 6 | 94.29%
Northumbrian Water | AVONDALE CSO | 6NW800866 | 222/B/0049 | 222/B/0049 |  | SO on sewer network | NU2383911581 | GB103022076350 | Aln from Edlingham Burn to Tidal Limit | ALN |  |  | Commissioned pre-2016 - full year data expected | 24 | 21 | 99.04%
Northumbrian Water | 4 AYCLIFFE AVENUE CSO | 6NW801313 | 235/1955 | 235/1955 |  | SO on sewer network | NZ3060059900 | GB103023075690 | Don from Source to Tidal Limit | DON |  |  | Commissioned pre-2016 - full year data expected | 64.5 | 31 | 99.41%
Northumbrian Water | AYCLIFFE STW WORKS | 6NW800770(1) | 253/1278 | 253/1278 | A2 | Storm tank at WwTW | NZ2822823495 | GB103025072596 | Skerne from Demons Beck to Tees | DEMONS BECK |  |  | Commissioned in 2020 - full year data expected | 242.1928 | 29 | 100%
Northumbrian Water | AYCLIFFE STW WORKS | 6NW800770(2) | 253/1278 | 253/1278 | A2 | Storm tank at WwTW | NZ2825323488 | GB103025072596 | Skerne from Demons Beck to Tees | DEMONS BECK |  |  | Commissioned in 2020 - full year data expected | 302.9719 | 29 | 100%
Northumbrian Water | B1285 STORAGE TANK | 6NW800405 | 255/1181 | 255/1181 |  | SO on sewer network | NZ4026047030 | GB103025075970 | Dalton Beck to North Sea | DALTON BURN |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | CORNSAY COLLIERY STORM SEWAGE OVERF | 6NW801047 | 244/0921 | 244/0921 |  | SO on sewer network | NZ1723043100 | GB103024077290 | Hedleyhope Burn from Source to Deerness | HEDLEYHOPE BURN |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.08%
Northumbrian Water | BACK ELM STREET CSO | 6NW801137 | 244/E/0216 | 244/E/0216 |  | SO on sewer network | NZ2138344981 | GB103024077551 | Browney from Smallhope Burn Deerness confl | RIVER BROWNEY |  |  | Commissioned pre-2016 - full year data expected | 6.25 | 7 | 96.19%
Northumbrian Water | BACK LANE COMBINED SEWER OVERFLOW | 6NW801339 | 245/1396 | 245/1396 |  | SO on sewer network | NZ2917050060 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | BROUGH'S GILL |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | BACK LODGE TERRACE CSO | 6NW800408 | 255/1207 | 255/1207 |  | SO on sewer network | NZ4108256147 | GB650301500002 | Tyne and Wear | NORTH SEA |  |  | Commissioned pre-2016 - full year data expected | 165 | 45 | 99.99%
Northumbrian Water | COTHERSTONE SEWAGE DISPOSAL WORKS BALDER COTTAGE CSO | 6NW800919 | 251/0925 | 251/0925 |  | SO on sewer network | NZ0091720008 | GB103025072240 | Balder Catchment (trib of Tees) | BALDER |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.73%
Northumbrian Water | BANK TOP CSO | 6NW801292 | 226/1181 | 226/1181 |  | SO on sewer network | NZ2778382259 | 5 | #N/A | RIVER BLYTH |  |  | Commissioned pre-2016 - full year data expected | 142.5 | 45 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | BARCLAYS A CSO ELVET | 6NW801271 | 245/0447 | 245/0447 |  | SO on sewer network | NZ2760642176 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | WEAR |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.98%
Northumbrian Water | THE LARCHES PUMPING STATION | 6NW800489 | 232/0990 | 232/0990 | 232/0990-01 | Storm discharge at pumping station | NY7731064460 | GB103023075532 | South Tyne from Tipalt Burn to Allen | SOUTH TYNE |  |  | Commissioned in 2020 - full year data expected | 12.3217 | 9 | 99.99%
Northumbrian Water | TOW HOUSE PUMPING STATION | 6NW800487 | 232/0991 | 232/0991 | 232/0991-01 | Storm discharge at pumping station | NY7680064330 | GB103023075532 | South Tyne from Tipalt Burn to Allen | SOUTH TYNE |  |  | Commissioned in 2020 - full year data expected | 217.0472 | 68 | 99.98%
Northumbrian Water | CATHEDRAL BANKS CSO Barkers Haugh CSO3 Court Lane West | 6NW801272 | 245/E/0659 | 245/E/0659 |  | SO on sewer network | NZ2759542214 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | River Wear |  |  | Commissioned pre-2016 - full year data expected | 0.25 | 1 | 99.99%
Northumbrian Water | BARKERS HAUGH NO 5 CSO Prebends Bridge | 6NW801265 | EPRNB3092AL | EPRNB3092AL |  | SO on sewer network | NZ2718241860 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | RIVER WEAR |  |  | Commissioned pre-2016 - full year data expected | 1.25 | 4 | 99.86%
Northumbrian Water | BARKERS HAUGH NO 8 CSO Freemans Place | 6NW801268 | EPRQB3897RB | EPRQB3897RB |  | SO on sewer network | NZ2749143026 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | RIVER WEAR |  |  | Commissioned pre-2016 - full year data expected | 344 | 80 | 99.76% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | BARKERS HAUGH CSO NO. 10 Orchard Drive | 6NW800339 | EPRJB3293AU | EPRJB3293AU |  | SO on sewer network | NZ2804143132 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | RIVER WEAR |  |  | Commissioned in 2016 - full year data expected | 44 | 35 | 98.95%
Northumbrian Water | BARKERS HAUGH STW | 6NW800767 | 245/1245 | 245/1245 |  | Storm tank at WwTW | NZ2807743394 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | WEAR |  |  | Commissioned in 2020 - full year data expected | 699.1294 | 69 | 99.99%
Northumbrian Water | BARNARD CASTLE STW CSO INLET | 6NW800146 | 25/02/1111 | 25/02/1111 | 25/02/1111-03 | Inlet SO at WwTW | NZ0582315450 | GB103025072512 | Tees from Percy Beck to River Greta | River Tees |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | BARNARD CASTLE STW Storm Tank | 6NW800715 | 25/02/1111 | 25/02/1111 | 25/02/1111-02 | Storm tank at WwTW | NZ0582315450 | GB103025072512 | Tees from Percy Beck to River Greta | River Tees |  |  | Commissioned in 2020 - full year data expected | 0.7 | 4 | 99.82%
Northumbrian Water | BARNINGHAM STW | 6NW800147 | 252/0364 | 252/0364 | A2 | Inlet SO at WwTW | NZ0860010700 | GB103025072150 | Aldbrough Beck from Source to Clow Beck | NOR BECK |  |  | Commissioned in 2020 - full year data expected | 151.4861 | 17 | 100%
Northumbrian Water | CHAPEL STREET CSO BARRINGTON STREET | 6NW801103 | 243/0930 | 243/0930 |  | SO on sewer network | NZ2037330858 | GB103024077464 | Wear from Gaunless to Browney | Unnamed tributary of the River Wear |  |  | Commissioned pre-2016 - full year data expected | 65.75 | 24 | 61.93% | Comms failure / issue | Scheduled
Northumbrian Water | BARTON SEWAGE TREATMENT WORKS CSO INLET | 6NW800160 | 25/02/1080 | 25/02/1080 | 25/02/1080-03 | Inlet SO at WwTW | NZ2313009050 | GB103025072040 | Barton Beck from Source to Clow Beck | BARTON BECK |  |  | June 2021 | 15.8722 | 6 | 99.74%
Northumbrian Water | BARTON SEWAGE TREATMENT WORKS Storm Tank | 6NW800752 | 25/02/1080 | 25/02/1080 | 25/02/1080-02 | Storm tank at WwTW | NZ2313009050 | GB103025072040 | Barton Beck from Source to Clow Beck | BARTON BECK |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | BARWICK STREET CSO | 6NW801507 | 255/1126 | 255/1126 |  | SO on sewer network | NZ4001646498 | GB103025075970 | Dalton Beck to North Sea | MURTON DENE |  |  | Commissioned pre-2016 - full year data expected | 9.75 | 21 | 89.87% | Comms failure / issue | Resolved - August
Northumbrian Water | BATES COLLIERY SPS | 6NW800574 | 226/1178 | 226/1178 | 226/1178-02 | Storm discharge at pumping station | NZ3051082520 | GB510302203200 | BLYTH (N) | RIVER BLYTH (SALINE ESTUARY) |  |  | Commissioned in 2020 - full year data expected | 256.3003 | 44 | 99.95%
Northumbrian Water | BEACON AVENUE SPS | 6NW800598 | 253/0237 | 253/0237 | A1 | Storm discharge at pumping station | NZ3629429041 | GB103025076070 | Skerne from Source to Carrs | REDCAR BECK |  |  | Commissioned pre-2016 - full year data expected | 1.25 | 2 | 96.67%
Northumbrian Water | BEADNELL(SWINHOE ROAD) SEWAGE PUMPN | 6NW800468 | 221/1070 | 221/1070 | 221/1070-01 | Storm discharge at pumping station | NU2265028980 | 249 | #N/A | UNNAMED COASTAL STREAM |  | Beadnell | Commissioned in 2018 - full year data expected | 22.7419 | 5 | 100%
Northumbrian Water | BEADNELL CAR PARK SEWAGE PUMPING SN | 6NW800473 | 221/1071 | 221/1071 | 221/1071-01 | Storm discharge at pumping station | NU2390028570 | GB620301100000 | Farne Islands to Newton Haven | NORTH SEA |  | Beadnell | Commissioned in 2019 - full year data expected | 115.2681 | 16 | 20.75% | Comms failure / issue | Scheduled
Northumbrian Water | BEADNELL HARBOUR SEWAGE PUMPING STN | 6NW800474 | 221/1072 | 221/1072 | 221/1072-01 | Storm discharge at pumping station | NU2390028570 | GB620301100000 | Farne Islands to Newton Haven | NORTH SEA |  | Beadnell | Commissioned in 2018 - full year data expected | 255.3789 | 40 | 100%
Northumbrian Water | PUMPING STATION NO4 BEAL BANK | 6NW800870 | 223/B/0222 | 223/B/0222 | 223/B/0222-01 | Storm discharge at pumping station | NU2510905551 | GB510302203000 | COQUET | COQUET |  | Warkworth & Amble Links | Commissioned pre-2016 - full year data expected | 2.3667 | 2 | 49.83% | Comms failure / issue | Resolved - November
Northumbrian Water | BEAMISH CSO | 6NW800292 | EPRBB3395WB | EPRBB3395WB |  | SO on sewer network | NZ2255253648 | GB103023075670 | Team from Source to Tyne | TRIBUTARY OF URPETH BURN |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | BEAUMONT HILL SSO | 6NW801334 | 25/03/1248 | 25/03/1248 |  | SO on sewer network | NZ2936018180 | GB103025072596 | Skerne from Demons Beck to Tees | UNNAMED TRIB OF SKERNE |  |  | Commissioned pre-2016 - full year data expected | 17.5 | 13 | 90.79%
Northumbrian Water | ELTRINGHAM CSO BEAUMONT WOOD | 6NW800943 | 233/1091 | 233/1091 |  | SO on sewer network | NZ0825062510 | GB103023075801 | Tyne from Watersmeet to Tidal Limit | COLD KETTLE BURN |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 98.29%
Northumbrian Water | BEDSIDE CSO | 6NW801319 | 226/1206 | 226/1206 |  | SO on sewer network | NZ2818082260 | GB510302203200 | BLYTH (N) | BLYTH |  |  | Commissioned pre-2016 - full year data expected | 236 | 45 | 96.54%
Northumbrian Water | CSO AT BEDESWAY | 6NW800374 | 235/1276 | 235/1276 |  | SO on sewer network | NZ3441265064 | GB510302310200 | TYNE | RIVER DON |  |  | Commissioned in 2018 - full year data expected | 245.7039 | 53 | 100%
Northumbrian Water | BEDFORD STREET CSO NTY057 | 6NW801480 | 235/1910 | 235/1910 |  | SO on sewer network | NZ3575468102 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 19.75 | 18 | 99.92%
Northumbrian Water | NEDDERTON CSO BEDLINGTON | 6NW801190 | 226/1266 | 226/1266 |  | SO on sewer network | NZ2497083200 | GB103022076230 | Sleek Burn / Hepscott Burn Source to Tidal Limit | GREEN LETCH |  |  | Commissioned pre-2016 - full year data expected | 18 | 19 | 59.56% | Comms failure / issue | Resolved - August
Northumbrian Water | BEECH HILL CSO | 6NW800892 | 233/D/0390 | 233/D/0390 |  | SO on sewer network | NY9258164111 | GB103023075801 | Tyne from Watersmeet to Tidal Limit | COCKSHAW BURN CULVERTED |  |  | Commissioned pre-2016 - full year data expected | 0.1 | 3 | 96.58%
Northumbrian Water | BEECH STREET CSO | 6NW801117 | 234/1058 | 234/1058 |  | SO on sewer network | NZ2094658966 | GB103023075670 | Team from Source to Tyne | BLACK BURN |  |  | Commissioned pre-2016 - full year data expected | 3 | 3 | 95.11%
Northumbrian Water | BEECHVILLE CSO | 6NW800291 | 245/1083 | 245/1083 |  | SO on sewer network | NZ2281349486 | GB103024077560 | Cong Burn from Source to Twizell Burn | CONG BURN |  |  | Commissioned in 2017 - full year data expected | 261.2081 | 51 | 80.82% | Comms failure / issue | Scheduled | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution
Northumbrian Water | BEEHIVE CSO | 6NW800367 | 226/1271 | 226/1271 |  | SO on sewer network | NZ3286273332 | GB103022076180 | Brierdene Burn from Source to North Sea | BRIERDENE BURN |  |  | Commissioned in 2017 - full year data expected | 211 | 44 | 99.21%
Northumbrian Water | BELFORD INDUTRIAL ESTATE PS. | 6NW800460 | 221/0934 | 221/0934 | 221/0934-02 | Storm discharge at pumping station | NU1260033560 | GB103022076430 | Newlands Burn Catchment (trib of Waren Burn) | NEWLANDS BURN |  |  | Commissioned in 2019 - full year data expected | 35.08 | 2 | 99.52%
Northumbrian Water | BELFORD SEWAGE TREATMENT WORKS CSO INLET | 6NW800115 | 221/1034 | 221/1034 | 221/1034-03 | Inlet SO at WwTW | NU1171033885 | GB103022076460 | Belford Burn from Source to Ross Low | BELFORD BURN |  |  | Commissioned in 2020 - full year data expected | 1520.4036 | 135 | 100%
Northumbrian Water | BELFORD SEWAGE TREATMENT WORKS CSO Storm Tank | 6NW800692 | 221/1034 | 221/1034 | 221/1034-02 | Storm tank at WwTW | NU1171033885 | GB103022076460 | Belford Burn from Source to Ross Low | BELFORD BURN |  |  | Commissioned in 2020 - full year data expected | 2331.1469 | 108 | 100%
Northumbrian Water | BELL BURN WOOD CSO WV042 | 6NW800287 | 243/E/0097 | 243/E/0097 |  | SO on sewer network | NZ2252131682 | GB103024077464 | Wear from Gaunless to Browney | BELL BURN |  |  | Commissioned in 2016 - full year data expected | 4 | 6 | 98.03%
Northumbrian Water | BELLINGHAM STW | 6NW800701 | 231/1086 | 231/1086 | A2 | Storm tank at WwTW | NY8372282933 | GB103023074960 | N Tyne from Tarset Burn to River Rede | NORTH TYNE |  |  | Commissioned in 2020 - full year data expected | 2803.88 | 145 | 100%
Northumbrian Water | BELLINGHAM STW | 6NW801630 | 231/1086 | 231/1086 | A3 | Inlet SO at WwTW | NY8372282933 | GB103023074960 | N Tyne from Tarset Burn to River Rede | RIVER NORTH TYNE |  |  | Commissioned pre-2016 - full year data expected | 135.25 | 37 | 99.43%
Northumbrian Water | BELMONT STW | 6NW800776 | 245/1246 | 245/1246 | 245/1246-03 | Storm tank at WwTW | NZ3041045290 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | UNNAMED TRIB. OF RIVER WEAR |  |  | Commissioned in 2020 - full year data expected | 237.5844 | 31 | 100%
Northumbrian Water | BENNETTS WALK CSO | 6NW800274 | EPRDP3923XT | EPRDP3923XT |  | Storm discharge at pumping station | NZ2023085839 | GB103022077061 | Wansbeck from Font to Bothal Burn | RIVER WANSBECK |  |  | Commissioned in 2020 - full year data expected | 6.0428 | 18 | 99.98%
Northumbrian Water | BENSHAM CSO | 6NW800918 | 235/1737 | 235/1737 |  | SO on sewer network | NZ2360162077 | GB510302310200 | TYNE | RIVER TEAM ESTUARINE WATERS |  |  | Commissioned pre-2016 - full year data expected | 51.5 | 20 | 99.01%
Northumbrian Water | BENSHAM HOSPITAL CSO | 6NW801184 | 235/2009 | 235/2009 |  | SO on sewer network | NZ2433260965 | GB103023075670 | Team from Source to Tyne | TEAM, RIVER |  |  | Commissioned pre-2016 - full year data expected | 3.5333 | 8 | 100%
Northumbrian Water | BENSHAM SIDINGS CSO | 6NW801182 | 235/1894 | 235/1894 |  | SO on sewer network | NZ2433260965 | GB103023075670 | Team from Source to Tyne | TEAM |  |  | Commissioned pre-2016 - full year data expected | 53.6344 | 28 | 8.344% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | BERRY EDGE ROAD CSO DER096 | 6NW800955 | 234/1137 | 234/1137 |  | SO on sewer network | NZ0907549831 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | UNNAMED TRIB OF DENE BURN |  |  | Commissioned pre-2016 - full year data expected | 12.5 | 21 | 99.38%
Northumbrian Water | BERWICK P S NO 7 (MAGDALENE FIELDS) | 6NW800459 | 210/1351 | 210/1351 | 210/1351-01 | Storm discharge at pumping station | NU0031054260 | GB650301440000 | Northumberland North | NORTH SEA |  |  | Commissioned in 2020 - full year data expected | 430.5014 | 109 | 100%
Northumbrian Water | BERWICK NO 4 SEWAGE PUMPING STATION | 6NW800845 | 210/1329 | 210/1329 | 210/1329-01 | Storm discharge at pumping station | NU0039052660 | GB510202110000 | TWEED | RIVER TWEED (SALINE ESTUARY) |  | Spittal | Commissioned pre-2016 - full year data expected | 2.2 | 2 | 55.54% | Comms failure / issue | N/A - Ongoing investigation
Northumbrian Water | BERWICK STW | 6NW800687 | 210/1273 | 210/1273 | A2 | Storm tank at WwTW | NT9800052450 | GB510202110000 | TWEED | RIVER TWEED (SALINE ESTUARY) |  | Spittal | Commissioned in 2019 - full year data expected | 54.465 | 11 | 6.702% | Installation set-up/design issue | Resolved - December
Northumbrian Water | BEVERLEY GARDENS CSO | 6NW801277 | NPSWQD009328 | NPSWQD009328 |  | SO on sewer network | NZ2780250303 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | RIVER WEAR |  |  | Commissioned pre-2016 - full year data expected | 6.75 | 11 | 98.47%
Northumbrian Water | BILLINGHAM STW CSO INLET | 6NW800192 | 254/1965 | 254/1965 |  | Inlet SO at WwTW | NZ4846025840 | GB510302509900 | Tees | NORTH SEA |  |  | Feb 2021 | 130.6261 | 44 | 99.91%
Northumbrian Water | BILLINGHAM STW CSO INLET High level outfall 1 to Greatham Creek | 6NW800190 | 254/1965 | 254/1965 | 254/1965-08 | Inlet SO at WwTW | NZ4846025840 | GB510302509900 | Tees | NORTH SEA |  |  | Commissioned in 2020 - full year data expected | 263.3619 | 52 | 100%
Northumbrian Water | BILLINGHAM STW CSO INLET High level outfall 2 to Cowbridge Beck | 6NW800191 | 254/1965 | 254/1965 | 254/1965-08 | Inlet SO at WwTW | NZ4846025840 | GB510302509900 | Tees | NORTH SEA |  |  | Feb 2021 | 0.27417 | 1 | 99.95%
Northumbrian Water | BILLINGHAM STW Storm Tank | 6NW800797 | 254/1965 | 254/1965 | 254/1965-06 | Storm tank at WwTW | NZ4846025840 | GB510302509900 | Tees | NORTH SEA |  |  | Commissioned in 2020 - full year data expected | 429.4425 | 52 | 100%
Northumbrian Water | BINCHESTER PLANTATION CSO | 6NW800276 | 243/0967 | 243/0967 |  | SO on sewer network | NZ2106631023 | GB103024077464 | Wear from Gaunless to Browney | RIVER WEAR |  |  | Commissioned in 2017 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | BIRTLEY STW CSO INLET | 6NW800165 | 235/1891 | 235/1891 | 235/1891-04 | Inlet SO at WwTW | NZ2604056690 | GB103023075670 | Team from Source to Tyne | TEAM |  |  | Jan 2021 | 24.5706 | 16 | 100%
Northumbrian Water | BIRTLEY STW Storm Tank | 6NW800764 | 235/1891 | 235/1891 | 235/1891-03 | Storm tank at WwTW | NZ2604056690 | GB103023075670 | Team from Source to Tyne | TEAM |  |  | Commissioned in 2020 - full year data expected | 415.5658 | 37 | 100%
Northumbrian Water | BISHOP MIDDLEHAM SEWAGE WORKS | 6NW800779 | 25/03/1221 | 25/03/1221 | A2 | Storm tank at WwTW | NZ3271030300 | GB103025072520 | Carrs from Source to Skerne | THE CARRS |  |  | Commissioned in 2020 - full year data expected | 285.0725 | 57 | 100%
Northumbrian Water | BISHOP STREET NORTH SSO M2 | 6NW854101M2 | 25/04/1701 | 25/04/1701 | A2 | SO on sewer network | NZ4489019240 | GB103025072595 | Tees from Skerne to Tidal Limit | RIVER TEES |  |  | Commissioned pre-2016 - full year data expected | 68.7333 | 49 | 99.96%
Northumbrian Water | BISHOP STREET NORTH SSO M3 | 6NW854101M3 | 25/04/1701 | 25/04/1701 | A1 | SO on sewer network | NZ4489019240 | GB103025072595 | Tees from Skerne to Tidal Limit | RIVER TEES |  |  | Commissioned in 2017 - full year data expected | 84.7 | 43 | 100%
Northumbrian Water | BISHOP STREET NORTH SSO M4 | 6NW854101M4 | 25/04/1701 | 25/04/1701 | A3 | SO on sewer network | NZ4489019240 | GB103025072595 | Tees from Skerne to Tidal Limit | RIVER TEES |  |  | Commissioned in 2017 - full year data expected | 0 | 0 | 100%
Northumbrian Water | BISHOPTON MILL PS | 6NW800603 | 25/04/1766 | 25/04/1766 | 25/04/1766-01 | Storm discharge at pumping station | NZ3791022550 | GB103025072360 | Billingham Beck from Bishopton Bck to Brierle | WHITTON BECK |  |  | Commissioned in 2019 - full year data expected | 466.9956 | 44 | 99.41%
Northumbrian Water | BISHOPTON ROAD CSO | 6NW801543 | 254/1379 | 254/1379 |  | SO on sewer network | NZ4377319734 | GB103025072550 | Lustrum Beck Catchment (trib of Tees) | LUSTRUM BECK |  |  | Commissioned pre-2016 - full year data expected | 354.25 | 39 | 99.87%
Northumbrian Water | BISHOPTON STW | 6NW800787 | 25/04/1750 | 25/04/1750 | A2 | Storm tank at WwTW | NZ3612021460 | GB103025072280 | Bishopton Beck from Source to Billingham Beck | BISHOPTON BECK |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | BLACK HORSE CSO | 6NW801651 | 243/1012 | 243/1012 |  | SO on sewer network | NZ3232034950 | GB103024077410 | Croxdale Beck from Source to Wear | COXHOE BECK |  |  | Commissioned pre-2016 - full year data expected | 33.75 | 34 | 99.35%
Northumbrian Water | BLACK LANE CSO | 6NW801240 | 235/1963 | 235/1963 |  | SO on sewer network | NZ2674457739 | GB103023075670 | Team from Source to Tyne | LONGACRE BURN |  |  | Commissioned pre-2016 - full year data expected | 2.75 | 6 | 55.31% | Comms failure / issue | Resolved - August
Northumbrian Water | BLACKETT STREET CSO | 6NW801416 | 235/1744 | 235/1744 |  | SO on sewer network | NZ3203065850 | GB510302310200 | TYNE | RIVER TYNE SALINE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 24 | 12 | 99.82%
Northumbrian Water | BLACKHALL MILL PUMPING STATION | 6NW800983 | 234/0918 | 234/0918 | 234/0918-01 | SO on sewer network | NZ1227956921 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | TONGUE BURN (DERWENT) |  |  | Commissioned pre-2016 - full year data expected | 7.75 | 6 | 99.97%
Northumbrian Water | BLADESIDE CSO | 6NW801020 | 241/1098 | 241/1098 |  | SO on sewer network | NZ1674335319 | GB103024077390 | Beechburn Beck (Trib of Wear) | CROOK BECK |  |  | Commissioned pre-2016 - full year data expected | 507.25 | 68 | 99.79% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | CSO AT BLAKEWELL ROAD | 6NW800824 | 210/0938 | 210/0938 |  | SO on sewer network | NT9947152814 | GB510202110000 | TWEED | TWEED ESTUARY |  | Spittal | Commissioned pre-2016 - full year data expected | 52.7 | 40 | 99.6%
Northumbrian Water | BLANCHLAND STW CSO INLET | 6NW800140 | 234/1069 | 234/1069 | C | Inlet SO at WwTW | NY9690050300 | GB103023074770 | Derwent from Nookton Burn to Burnhope Burn | RIVER DERWENT |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | BLANCHLAND STW Storm Tank | 6NW800708 | 234/1069 | 234/1069 | B | Storm tank at WwTW | NY9690050300 | GB103023074770 | Derwent from Nookton Burn to Burnhope Burn | RIVER DERWENT |  |  | Commissioned in 2020 - full year data expected | 59.6083 | 26 | 91.51%
Northumbrian Water | BLANEY ROW PUMPING STATION | 6NW801012 | 235/1727 | 235/1727 | 235/1727-01 | SO on sewer network | NZ1535365250 | GB510302310200 | TYNE | RIVER TYNE SALINE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 14.75 | 6 | 95.24%
Northumbrian Water | BLANKNEY CLOSE CSO | 6NW801608 | 256/1045 | 256/1045 |  | SO on sewer network | NZ6114915290 | GB103025071970 | Skelton Beck Catch (Saltburn) trib of North Sea | TRIBUTARY OF CHAPEL BECK |  |  | Commissioned pre-2016 - full year data expected | 12.75 | 4 | 99.99%
Northumbrian Water | BLAYDON BANK CSO | 6NW801057 | 235/1438 | 235/1438 |  | SO on sewer network | NZ1822563606 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 158.4667 | 59 | 99.97% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | BLAYDON BURN WAGONWAY CSO | 6NW800256 | 233/1228 | 233/1228 |  | SO on sewer network | NZ1809563602 | GB103023074791 | Blaydon Burn | RIVER TYNE SALINE ESTUARY |  |  | Commissioned in 2019 - full year data expected | 0.98111 | 4 | 100%
Northumbrian Water | BLAYDON METALS NO 1 CSO | 6NW801067 | 235/1685 | 235/1685 |  | SO on sewer network | NZ1867963540 | GB510302310200 | TYNE | TYNE SALINE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 24.9333 | 20 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | BLAYDON METALS NO 2 CSO | 6NW801068 | 235/1686 | 235/1686 |  | SO on sewer network | NZ1869463551 | GB510302310200 | TYNE | TYNE |  |  | Commissioned pre-2016 - full year data expected | 173.8667 | 36 | 100%
Northumbrian Water | BLEACH GREEN FARM CSO | 6NW801158 | 244/0999 | 244/0999 |  | SO on sewer network | NZ2369041750 | GB103024077280 | Deerness from Hedleyhope Burn to Browney | RIVER DEERNESS |  |  | Commissioned pre-2016 - full year data expected | 132 | 17 | 99.93%
Northumbrian Water | BLUE BELL INN CSO | 6NW801249 | 235/1973 | 235/1973 |  | SO on sewer network | NZ2632065410 | GB103023075780 | Ouse Burn from Source to Tyne | OUSE BURN |  |  | Commissioned pre-2016 - full year data expected | 43.5 | 16 | 99.68%
Northumbrian Water | BLUEHOUSE GILL CSO | 6NW800425 | 255/1075 | 255/1075 |  | SO on sewer network | NZ4628939473 | 367 | #N/A | BLUEHOUSE GILL (NORTH SEA) |  | Crimdon | Commissioned in 2018 - full year data expected | 922.7839 | 70 | 99.99%
Northumbrian Water | BLYTH NO5 SPS | 6NW800581 | 226/1176 | 226/1176 | 226/1176-02 | Storm discharge at pumping station | NZ3158081840 | GB510302203200 | BLYTH (N) | RIVER BLYTH (SALINE ESTUARY) |  |  | Commissioned in 2020 - full year data expected | 1295.8006 | 89 | 100%
Northumbrian Water | BLYTH NO6 SPS | 6NW800575 | 226/1177 | 226/1177 | 226/1177-02 | Storm discharge at pumping station | NZ3101082280 | GB510302203200 | BLYTH (N) | RIVER BLYTH(SALINE ESTUARY) |  |  | Commissioned in 2020 - full year data expected | 60.1119 | 110 | 99.95%
Northumbrian Water | BLYTH (NEW) SEWAGE TREATMENT WORKS | 6NW800773 | 226/1179 | 226/1179 | A2 | Storm tank at WwTW | NZ2948982336 | GB510302203200 | BLYTH (N) | RIVER BLYTH (SALINE ESTUARY) |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | BOATHOUSE LANE PUMPING STATION | 6NW800630 | 254/1366 | 254/1366 | A | Storm discharge at pumping station | NZ4467018070 | GB103025072595 | Tees from Skerne to Tidal Limit | TEES ESTUARY |  |  | Commissioned in 2020 - full year data expected | 35.7936 | 20 | 99.97%
Northumbrian Water | BODLEWELL LANE CSO | 6NW801513 | 245/0983 | 245/0983 |  | SO on sewer network | NZ4031057394 | GB510302402900 | WEAR | WEAR ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 186.5 | 39 | 92.71% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | BOLDON COLLIERY FENWICK STREET CSO | 6NW800372 | EPRCB3096NZ | EPRCB3096NZ |  | SO on sewer network | NZ3427462728 | GB103023075690 | Don from Source to Tidal Limit | RIVER DON |  |  | Commissioned in 2020 - full year data expected | 0.5 | 1 | 69.32% | Sensor failure / issue | Resolved - August
Northumbrian Water | BOLDON COLLIERY SOUTH (N0'7) CSO | 6NW801455 | EPRCB3096RW | EPRCB3096RW |  | SO on sewer network | NZ3543562359 | GB103023075690 | Don from Source to Tidal Limit | RIVER DON |  |  | Commissioned pre-2016 - full year data expected | 4.5 | 5 | 73.1% | Comms failure / issue | Resolved - March
Northumbrian Water | BOLDRON STW | 6NW800144 | 252/0073 | 252/0073 | A2 | Inlet SO at WwTW | NZ0381114407 | GB103025072512 | Tees from Percy Beck to River Greta | Tributary of Manifold Beck |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | BONDISLE WAY CSO | 6NW800910 | 241/1090 | 241/1090 |  | SO on sewer network | NZ0003338462 | GB103024077461 | Wear from Middlehope Burn to Houselop Beck | RIVER WEAR |  |  | Commissioned pre-2016 - full year data expected | 23.5 | 21 | 97.17%
Northumbrian Water | BOTHAL CSO THE TUNNELS CM036 | 6NW801173 | 225/1068 | 225/1068 |  | SO on sewer network | NZ2331387574 | GB103022077030 | Bothal Burn Catchment (trib of Wansbeck) | BOTHAL BURN |  |  | Commissioned pre-2016 - full year data expected | 19 | 20 | 99.98%
Northumbrian Water | BOTHAL COTTAGES | 6NW801221 | 225/1028 | 225/1028 |  | SO on sewer network | NZ2569086890 | GB103022077062 | Wansbeck from Bothal Burn to North Sea | UNNAMED TRIB OF R WANSBECK |  |  | Commissioned pre-2016 - full year data expected | 1.5 | 2 | 90.82%
Northumbrian Water | BOULMER SEWAGE TREATMENT WORKS | 6NW800869 | 221/1035 | 221/1035 | 221/1035-03 | Inlet SO at WwTW | NU2680015660 | GB650301500001 | Northumberland South | NORTH SEA |  |  | Commissioned pre-2016 - full year data expected | 995.25 | 82 | 99.46% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | BOURN LEA CSO CH087 | 6NW801661 | 245/1376 | 245/1376 |  | SO on sewer network | NZ3238851928 | GB103024077630 | Herrington Burn from Source to Lumley Park Burn | HERRINGTON BURN |  |  | Commissioned pre-2016 - full year data expected | 3.4333 | 4 | 66.14% | Comms failure / issue | Resolved - October
Northumbrian Water | BOWBURN BRIDGE PS | 6NW800570 | 243/0980 | 243/0980 | 243/0980-01 | Storm discharge at pumping station | NZ3059837810 | GB103024077410 | Croxdale Beck from Source to Wear | BOWBURN BECK |  |  | Commissioned pre-2016 - full year data expected | 527.75 | 55 | 99.99%
Northumbrian Water | BOWBURN STW (2002) CSO INLET | 6NW800171 | 243/0970 | 243/0970 | A5 | Inlet SO at WwTW | NZ3009836993 | GB103024077410 | Croxdale Beck from Source to Wear | BOWBURN BECK |  |  | Commissioned in 2020 - full year data expected | 424.4756 | 57 | 99.81%
Northumbrian Water | BOWBURN STW (2002) Storm Tank | 6NW800775 | 243/0970 | 243/0970 | A2 | Storm tank at WwTW | NZ3009836993 | GB103024077410 | Croxdale Beck from Source to Wear | BOWBURN BECK |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | BOWES SEWAGE TREATMENT WORKS | 6NW800710 | 25/02/1105 | 25/02/1105 | 25/02/1105-02 | Storm tank at WwTW | NY9978013150 | GB103025072140 | Greta from Sleightholme Beck to Eller Beck | RIVER GRETA |  |  | Commissioned in 2020 - full year data expected | 440.2189 | 70 | 98.71%
Northumbrian Water | BOWESFIELD LANE CSO | 6NW800418 | 254/1266 | 254/1266 |  | SO on sewer network | NZ4467816863 | GB103025072595 | Tees from Skerne to Tidal Limit | RIVER TEES ESTUARY (SALINE) |  |  | Commissioned in 2017 - full year data expected | 0 | 0 | 70.89% | Sensor failure / issue | Resolved - March
Northumbrian Water | BRADBURY STW | 6NW800174 | 253/1277 | 253/1277 | A2 | Inlet SO at WwTW | NZ3195028490 | GB103025072430 | Skerne from Carrs to Woodham Burn | RIVER SKERNE |  |  | Commissioned in 2020 - full year data expected | 98.8833 | 31 | 99.95%
Northumbrian Water | BRAFFERTON CSO - REAR OF HALL GARTH HOTEL | 6NW801675 | #TBC | Permit Anomaly | To be permitted for storm | SO on sewer network | NZ2919620613 | GB103025072290 | Dene Beck Catchment (trib of Skerne) | River Skerne |  |  | Commissioned pre-2016 - full year data expected | 227.25 | 17 | 93.44%
Northumbrian Water | BRAN SANDS TREATMENT WORKS | 6NW800197 | 254/1920 | 254/1920 | 254/1920-07 | Inlet SO at WwTW | NZ5614024090 | GB103025072320 | Tees Estuary (S Bank) | DABHOLM GUT |  |  | Commissioned in 2020 - full year data expected | 625.5358 | 120 | 99.64%
Northumbrian Water | BRANCEPETH STW | 6NW800750 | 243/1024 | 243/1024 | A2 | Storm tank at WwTW | NZ2253037520 | GB103024077420 | Brancepeth Beck from Source to Wear | BRANCEPETH BECK |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | BRANDYWELL CSO | 6NW800822 | 210/1359 | 210/1359 |  | SO on sewer network | NT9999851989 | GB510202110000 | Tweed water body | RIVER TWEED (SALINE ESTUARY) |  | Spittal | Commissioned pre-2016 - full year data expected | 65.1586 | 51 | 99.9%
Northumbrian Water | BRANXTON STW | 6NW800101 | 210/0039 | 210/0039 | A2 | Inlet SO at WwTW | NT8915037910 | GB102021072990 | Pallins Burn Catch (trib of Till) | PALLINS BURN |  |  | Commissioned in 2020 - full year data expected | 347.3667 | 25 | 78.11% | Comms failure / issue | Resolved - August
Northumbrian Water | SOUTHERN MAIN DRAINAGE SEWER BRENDA ROAD CSO | 6NW801585 | 255/A/0940 | 255/A/0940 |  | SO on sewer network | NZ5137029250 | 368 | #N/A | STELL, TRIBUTARY OF |  | Seaton Carew (Centre) | Commissioned pre-2016 - full year data expected | 0 | 0 | 100%
Northumbrian Water | BRENDA ROAD/PARK VIEW CSO | 6NW801586 | 25/05/5033 | 25/05/5033 |  | SO on sewer network | NZ5100930078 | GB650301500005 | Tees Coastal | A culverted section of The Stell |  | Seaton Carew (Centre) | Commissioned pre-2016 - full year data expected | 0.26667 | 2 | 99.97%
Northumbrian Water | BRIARDALE CSO | 6NW801218 | NPSWQD000519 | NPSWQD000519 |  | SO on sewer network | NZ2595282604 | GB103022076230 | Sleek Burn / Hepscott Burn Source to Tidal Limit | UNNAMED TRIB SLEEK BURN |  |  | Commissioned pre-2016 - full year data expected | 2.25 | 4 | 99.92%
Northumbrian Water | BRIARDALE ROAD CSO | 6NW801350 | 226/1057 | 226/1057 |  | SO on sewer network | NZ2960382326 | 5 | #N/A | River Blyth Estuary |  |  | Commissioned pre-2016 - full year data expected | 73.75 | 40 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | BRIDGE END COTTAGES CSO | 6NW800908 | 233/1244 | 233/1244 |  | SO on sewer network | NY9889964240 | GB103023075801 | Tyne from Watersmeet to Tidal Limit | RIVER TYNE |  |  | Commissioned pre-2016 - full year data expected | 6.75 | 12 | 99.84%
Northumbrian Water | BRIDGE END PS | 6NW800501 | 226/1078 | 226/1078 | A1 | Storm discharge at pumping station | NZ0801071810 | GB103022076840 | Pont from Fenwick Burn to Med Burn | PONT |  |  | Commissioned in 2020 - full year data expected | 0 | 0 | 100%
Northumbrian Water | BRIDGE STREET PUMPING STATION | 6NW800660 | 25/05/5040 | 25/05/5040 | 25/05/5040-02 | Storm discharge at pumping station | NZ5185032480 | GB650301500005 | Tees Coastal | NORTH SEA |  |  | Commissioned in 2020 - full year data expected | 11.5417 | 40 | 100%
Northumbrian Water | BRIERDENE PUMPING STATION | 6NW800378 | 235/1241 | 235/1241 | 235/1241-2.1 (Storm Sewage) | Storm discharge at pumping station | NZ3596074310 | GB650301500002 | Tyne and Wear | NORTH SEA |  | Whitley Bay | Commissioned in 2019 - full year data expected | 125.1397 | 35 | 99.94%
Northumbrian Water | BRINKBURN CRESCENT CSO (SU28) | 6NW801430 | 245/1358 | 245/1358 |  | SO on sewer network | NZ3291950302 | GB103024077580 | Lumley Park Burn from Source to Herrington Burn | MOORS BURN, TRIB LUMLEY PARK |  |  | Commissioned pre-2016 - full year data expected | 3.5 | 7 | 99.98%
Northumbrian Water | BRINKBURN SSO | 6NW801655 | 245/1355 | 245/1355 |  | SO on sewer network | NZ3264149388 | GB103024077580 | Lumley Park Burn from Source to Herrington Burn | RED BURN |  |  | Commissioned pre-2016 - full year data expected | 2.25 | 3 | 99.99%
Northumbrian Water | BROAD CHARE CSO | 6NW800316 | 235/1919 | 235/1919 |  | SO on sewer network | NZ2551163934 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | Commissioned in 2018 - full year data expected | 184.1333 | 37 | 39.8% | Comms failure / issue | Scheduled | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | BROADWAY JUNCTION NORWOOD ROAD CSO | 6NW801071 | EPRBB3993EE | EPRBB3993EE |  | SO on sewer network | NZ1904665266 | 8 | #N/A | SUGLEY DENE |  |  | Commissioned pre-2016 - full year data expected | 0.66667 | 1 | 100%
Northumbrian Water | BROADWAY ROAD CSO | 6NW801094 | EPRBB3999AQ | EPRBB3999AQ |  | SO on sewer network | NZ1990465237 | 8 | #N/A | TIDAL RIVER TYNE |  |  | Commissioned pre-2016 - full year data expected | 0.76667 | 2 | 100%
Northumbrian Water | BLACKWELL Broken SCAR PS | 6NW800530 | 252/1015 | QR.252/1015 | A | Storm discharge at pumping station | NZ2590013700 | GB103025072190 | Tees from River Greta to River Skerne | River Tees |  |  | Commissioned in 2020 - full year data expected | 0.036111 | 2 | 99.74%
Northumbrian Water | BROOKE AVENUE (NO20) STY049 CSO | 6NW801468 | EPRBB3792AU | EPRBB3792AU |  | SO on sewer network | NZ3586962022 | GB103023075690 | Don from Source to Tidal Limit | RIVER DON |  |  | Commissioned pre-2016 - full year data expected | 78.5 | 44 | 99.34% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | BROOM PARK OLD WORKS CSO | 6NW801179 | 244/0936 | 244/0936 |  | SO on sewer network | NZ2495541484 | GB103024077280 | Deerness from Hedleyhope Burn to Browney | RELLEY GILL |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | BROOMHAUGH SEWAGE TREATMENT WORKS | 6NW800713 | 233/1200 | 233/1200 | A2 | Storm tank at WwTW | NZ0282062100 | GB103023075801 | Tyne from Watersmeet to Tidal Limit | RIVER TYNE |  |  | Commissioned in 2020 - full year data expected | 856.3631 | 69 | 96.96%
Northumbrian Water | BROTTON MILLHOLME DRIVE | 6NW801622 | 25/06/0985 | 25/06/0985 |  | SO on sewer network | NZ6774120260 | GB103025071960 | Saltburn Gill Catch trib of North Sea | TRIB OF MILLHOLME BECK |  | Saltburn Pier | Commissioned pre-2016 - full year data expected | 88.5 | 13 | 93.65%
Northumbrian Water | BROWNEY LANE CSO | 6NW801176 | 244/1003 | 244/1003 |  | SO on sewer network | NZ2500538681 | GB103024077552 | Browney from Deerness confl to Wear | UNNAMED TRIB. OF RIVER BROWNEY |  |  | Commissioned pre-2016 - full year data expected | 333 | 51 | 99.84% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | BROWNEY STW | 6NW800760 | 244/0985 | 244/0985 | A2 | Storm tank at WwTW | NZ2587038500 | GB103024077552 | Browney from Deerness confl to Wear | BROWNEY |  |  | Commissioned in 2020 - full year data expected | 153.7722 | 24 | 55.25% | Comms failure / issue | Resolved - October
Northumbrian Water | BROWNS BRIDGE CSO | 6NW801542 | 254/1833 | 254/1833 |  | SO on sewer network | NZ4377519746 | GB103025072550 | Lustrum Beck Catchment (trib of Tees) | THE LUSTRUM BECK |  |  | Commissioned pre-2016 - full year data expected | 104.5 | 14 | 99.93%
Northumbrian Water | BROWNS POINT CSO | 6NW800394 | 235/1793 | 235/1793 |  | SO on sewer network | NZ3648071540 | GB650301500002 | Tyne and Wear | NORTH SEA |  | Cullercoats | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
Northumbrian Water | BRUS SEWAGE PUMPING STATION | 6NW800652 | 255/5021 | QC.25/05/5021 | A | Storm discharge at pumping station | NZ5047635589 / NZ5053835695 | 368 | #N/A | North Sea |  |  | Commissioned in 2020 - full year data expected | 444.9869 | 49 | 100%
Northumbrian Water | BT41 MAIN STREET NO 4 CSO | 6NW800827 | 210/0940 | 210/0940 |  | SO on sewer network | NZ 50538 35695 | 368 | #N/A | RIVER TWEED ESTUARY |  | Spittal | Commissioned pre-2016 - full year data expected | 79.2333 | 31 | 73.67% | Comms failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | WOOLSINGTON SEWAGE SYSTEM BULLOCKS STEADS CSO | 6NW801124 | 235/1954 | 235/1954 |  | SO on sewer network | NZ2059070020 | GB103023075780 | Ouse Burn from Source to Tyne | OUSE BURN |  |  | Commissioned pre-2016 - full year data expected | 8.5 | 3 | 99.99%
Northumbrian Water | BURDON MAIN ROW CSO | 6NW801478 | 235/2006 | 235/2006 |  | SO on sewer network | NZ3558767688 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 6 | 12 | 99.99%
Northumbrian Water | BURDON ROAD CSO | 6NW800397 | 235/1279 | 235/1279 |  | SO on sewer network | NZ3659561997 | GB103023075690 | Don from Source to Tidal Limit | DON TRIBUTARY |  |  | Commissioned pre-2016 - full year data expected | 130.0667 | 33 | 99.93%
Northumbrian Water | BURN CLOSES CSO | 6NW801395 | 235/1776 | 235/1776 |  | SO on sewer network | NZ3115366916 | GB103023075760 | Wallsend Burn (Trib of Tyne) | WALLSEND BURN ESTUARINE WATERS |  |  | Commissioned pre-2016 - full year data expected | 793 | 100 | 98.54% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | BURNHOPE P.S. CSO & CER | 6NW801084 | 245/A/0575 | 245/A/0575 | 245/A/0575-B(1) Storm Sewage | SO on sewer network | NZ1932048470 | GB103024077560 | Cong Burn from Source to Twizell Burn | IBBETSONS' SIKE (RIVER WEAR) |  |  | Commissioned pre-2016 - full year data expected | 44.5 | 22 | 69.65% | Comms failure / issue | Resolved - April | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | BURNISTON DRIVE PS | 6NW801639 | 243/0892 | Permit Anomaly - EO permit 243/0892 | To be permitted for storm | Storm discharge at pumping station | NZ1923435151 | GB103024077464 | Wear from Gaunless to Browney | Willington Burn |  |  | Commissioned pre-2016 - full year data expected | 1807.75 | 126 | 97.5% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
Northumbrian Water | BURNIP ROAD CSO | 6NW801501 | 255/0509 | 255/0509 |  | SO on sewer network | NZ3920147770 | GB103025075970 | Dalton Beck to North Sea | DALTON DENE |  | Seaham Hall | Commissioned pre-2016 - full year data expected | 10.5 | 21 | 100%
Northumbrian Water | BURNOPFIELD CSO | 6NW801051 | 234/1053 | 234/1053 |  | SO on sewer network | NZ1750757658 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | LEAPMILL BURN |  |  | Commissioned pre-2016 - full year data expected | 319 | 50 | 91.68%
Northumbrian Water | BURNSIDE CSO | 6NW801092 | 235/1916 | 235/1916 |  | SO on sewer network | NZ1918865935 | 8 | #N/A | SUGLEY DENE |  |  | Commissioned pre-2016 - full year data expected | 2.0667 | 3 | 99.99%
Northumbrian Water | BURTON BECK CSO | 6NW801175 | 243/0974 | 243/0974 |  | SO on sewer network | NZ2462433890 | GB103024077350 | Valley Burn from Source to Wear | BURTON BECK |  |  | Commissioned pre-2016 - full year data expected | 29.5 | 23 | 99.59%
Northumbrian Water | BUSTY BANK STORM SEWAGE OVERFLOW | 6NW801052 | 234/0951 | 234/0951 |  | SO on sewer network | NZ1760057070 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | LEAPMILL BURN |  |  | Commissioned pre-2016 - full year data expected | 1.5 | 3 | 99.97%
Northumbrian Water | BUSTY BANK CSO | 6NW801053 | 234/0992 | 234/0992 |  | SO on sewer network | NZ1765057280 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | LEAPMILL BURN |  |  | Commissioned pre-2016 - full year data expected | 9.75 | 8 | 53.45% | Comms failure / issue | Scheduled
Northumbrian Water | BUSTY BANK CSO | 6NW801054 | 234/1016 | 234/1016 |  | SO on sewer network | NZ1770057190 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | LEAPMILL BURN TRIB |  |  | Commissioned pre-2016 - full year data expected | 1 | 3 | 99.99%
Northumbrian Water | BUTSFIELD LANE CSO DER092 | 6NW800975 | 244/1011 | 244/1011 |  | SO on sewer network | NZ1218648274 | GB103024077330 | Smallhope Burn from Source to Browney, Stocke | SMALLHOPE BURN |  |  | Commissioned pre-2016 - full year data expected | 162.25 | 59 | 99.27% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution
Northumbrian Water | BUTTERKNOWLE SEWAGE TREATMENT WORKS | 6NW800719 | 242/1070 | 242/1070 | A2 | Storm tank at WwTW | NZ1178325593 | GB103024072690 | Gaunless from Source to Hummer Beck | GAUNLESS |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | BUTTERYHAUGH PS | 6NW800484 | 231/0965 | 231/0965 | 231/0965-01 | Storm discharge at pumping station | NY6320092950 | GB103023075081 | N Tyne from Source to Lewis Burn | NORTH TYNE |  |  | Commissioned in 2020 - full year data expected | 122.1728 | 17 | 98.6%
Northumbrian Water | BYDALE SCHOOL CSO | 6NW801615 | 25/06/1019 | 25/06/1019 |  | SO on sewer network | NZ6297222796 | GB650301500005 | Tees Coastal | NORTH SEA |  | Marske | Commissioned pre-2016 - full year data expected | 44.4667 | 31 | 100%
Northumbrian Water | BYERS GREEN PUMPING STATION | 6NW800525 | 243/0959 | 243/0959 | 243/0959-02 | Storm discharge at pumping station | NZ2199034710 | GB103024077464 | Wear from Gaunless to Browney | RIVER WEAR |  |  | Commissioned in 2020 - full year data expected | 168.0689 | 28 | 85.05% | Installation set-up/design issue | Resolved - December
Northumbrian Water | CALDBECK CL BELMONT ST ANTHONYS CSO | 6NW800340 | 235/1324 | 235/1324 |  | SO on sewer network | NZ2890162949 | GB510302310200 | TYNE | RIVER TYNE ESTUARY |  |  | Commissioned in 2018 - full year data expected | 38.0706 | 29 | 100%
Northumbrian Water | CALDBECK AVENUE/POTTERY BANK CSO | 6NW801317 | 235/1325 | 235/1325 |  | SO on sewer network | NZ2890162949 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | Commissioned in 2018 - full year data expected | 1.9417 | 4 | 89.86% | Installation set-up/design issue | Resolved - September
Northumbrian Water | CALDBECK AVE POTTERY BANK CSO | 6NW800341 | 235/1326 | 235/1326 |  | SO on sewer network | NZ2890162949 | GB510302310200 | TYNE | RIVER TYNE ESTUARY |  |  | Commissioned in 2018 - full year data expected | 154.4244 | 27 | 100%
Northumbrian Water | CALEDONIAN ST / WILLIAM ST D17-103 STY056 | 6NW801672 | #TBC | Permit Anomaly | To be permitted for storm | SO on sewer network | NZ3063565667 | GB510302310200 | TYNE | River Tyne |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | CALF FALLOW LANE SPS | 6NW800626 | 25/04/1790 | 25/04/1790 | 25/04/1790-01 | Storm discharge at pumping station | NZ4392022940 | GB103025076010 | Billingham Beck from Brierley Beck to Tees Es | UNNAMED TRIB OF BILLINGHAM BEK |  |  | Commissioned pre-2016 - full year data expected | 6.75 | 4 | 82.67% | Comms failure / issue | Resolved - March
Northumbrian Water | CALIFORNIA ROW CSO | 6NW800227 | 251/0863 | 251/0863 |  | SO on sewer network | NY9513224887 | GB103025072511 | Tees from Maize Beck to Percy Beck | RIVER TEES |  |  | Commissioned in 2017 - full year data expected | 0.75 | 3 | 96.2%
Northumbrian Water | CAMBOIS SEWAGE TREATMENT WORKS | 6NW800170 | 226/1119 | 226/1119 | 226/1119-03 | Inlet SO at WwTW | NZ3283084320 | GB650301500002 | Tyne and Wear | THE NORTH SEA |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | CAR PARK CSO | 6NW801626 | 210/1344 | 210/1344 |  | SO on sewer network | NU0018151930 | GB510202110000 | TWEED | RIVER TWEED (SALINE ESTUARY) |  | Spittal | Commissioned pre-2016 - full year data expected | 99.1667 | 38 | 100%
Northumbrian Water | CARGO FLEET STW (OUTLET B) | 6NW800656 | 254/1514 | QR.25/04/1514 | 25/04/1514 S3 | Storm discharge at pumping station | NZ5150020830 | GB510302509900 | TEES | River Tees |  |  | Commissioned in 2020 - full year data expected | 24.1903 | 20 | 98.44%
Northumbrian Water | CARGO FLEET STW (OUTLET B) | 6NW800657 | 254/1514 | QR.25/04/1514 | 25/04/1514 S2 | Storm discharge at pumping station | NZ5158120488 | GB510302509900 | TEES | Ormsby Beck |  |  | Commissioned in 2020 - full year data expected | 737.4608 | 66 | 98.6%
Northumbrian Water | CARLTON & REDMARSHALL STW | 6NW800790 | 25/04/1706 | 25/04/1706 | 25/04/1706-03 | Storm tank at WwTW | NZ3848022230 | GB103025072360 | Billingham Beck from Bishopton Bck to Brierle | WHITTON BECK |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | CARLTON IN CLEVELAND STW | 6NW800194 | 25/04/1800 | 25/04/1800 | A2 | Inlet SO at WwTW | NZ5066004980 | GB103025071880 | Leven from Tame to River Tees | ALUM BECK LEVEN CATCHMENT |  |  | Commissioned in 2020 - full year data expected | 260.585 | 67 | 99.92%
Northumbrian Water | CARLTON PUMPING STATION | 6NW800611 | 254/D/0172 | 254/D/0172 | A1 | Storm discharge at pumping station | NZ3946621661 | GB103025072360 | Billingham Beck from Bishopton Bck to Brierle | LETCH BECK |  |  | Commissioned in 2019 - full year data expected | 650.7692 | 55 | 99.8%
Northumbrian Water | CAROLINE STREET CSO | 6NW801128 | EPRAB3593AS | EPRAB3593AS |  | SO on sewer network | NZ2132828289 | GB103024072730 | Gaunless from Hummer Beck to Wear | RIVER GAUNLESS |  |  | Commissioned pre-2016 - full year data expected | 3.5 | 8 | 99.99%
Northumbrian Water | CASSOP STW | 6NW800783 | 243/1016 | 243/1016 | 243/1016-02 | Storm tank at WwTW | NZ3412038370 | GB103024077470 | Old Durham Beck from Chapman Beck to Wear | CHAPMAN BECK |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | FORMER CASTLE DENE SDW SSO | 6NW801341 | 245/E/0592 | 245/E/0592 |  | SO on sewer network | NZ2954050630 | GB103024077570 | Lumley Park Burn from Herrington Burn to R Wear | LUMLEY PARK BURN |  |  | Commissioned pre-2016 - full year data expected | 5.75 | 2 | 96.8%
Northumbrian Water | MORPETH CSO E CASTLE SQUARE | 6NW800273 | 225/F/0525 | 225/F/0525 |  | SO on sewer network | NZ2005285840 | GB103022077061 | Wansbeck from Font to Bothal Burn | WANSBECK |  |  | October 2021 | 11.75 | 4 | 95.48%
Northumbrian Water | CASTLE TERRACE 1 CSO | 6NW800835 | 210/1356 | 210/1356 |  | SO on sewer network | NT9927653342 | GB510202110000 | TWEED | RIVER TWEED (SALINE ESTUARY) |  | Spittal | Commissioned pre-2016 - full year data expected | 106.9 | 46 | 99.65%
Northumbrian Water | CASTLE TERRACE NO2 (BT341) CSO | 6NW801679 | NPSWQD000697 | WQD000697 |  | SO on sewer network | NT9927653342 | GB510202110000 | TWEED | RIVER TWEED (SALINE ESTUARY) |  | Spittal | Commissioned in 2017 - full year data expected | 0 | 0 | 47.26% | Comms failure / issue | Resolved - July
Northumbrian Water | CASTLE VALE SPS | 6NW800457 | 210/1249 | 210/1249 | A1 | Storm discharge at pumping station | NT9937053130 | 3 | #N/A | RIVER TWEED (SALINE ESTUARY) |  | Spittal | Commissioned in 2019 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | CASTLESIDE CSO | 6NW800942 | 234/1105 | 234/1105 |  | SO on sewer network | NZ0886049980 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | DENE BURN (RIVER DERWENT) |  |  | Commissioned pre-2016 - full year data expected | 1.5 | 5 | 65.67% | Comms failure / issue | Resolved - December
Northumbrian Water | CASTLETON WALK CSO | 6NW801555 | 254/1418 | 254/1418 |  | SO on sewer network | NZ4470715956 | GB103025072595 | Tees from Skerne to Tidal Limit | TEES |  |  | Commissioned pre-2016 - full year data expected | 8.5333 | 16 | 99.84%
Northumbrian Water | CASTLETOWN WAY SPS | 6NW800599 | 245/0937 | 245/0937 | A1 | Storm discharge at pumping station | NZ3687058200 | 9 | #N/A | TRIB OF TIDAL WEAR |  |  | Commissioned in 2020 - full year data expected | 212.0808 | 46 | 99.98%
Northumbrian Water | CATHEDRAL BANKS CSO | 6NW800331 | 245/1336 | 245/1336 |  | SO on sewer network | NZ2725242302 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | RIVER WEAR |  |  | Commissioned pre-2016 - full year data expected | 1.25 | 3 | 99.99%
Northumbrian Water | CATTLE MARKET B SSO | 6NW801130 | 242/1045 | 242/1045 |  | SO on sewer network | NZ2145028980 | GB103024072730 | Gaunless from Hummer Beck to Wear | RIVER GAUNLESS |  |  | Commissioned pre-2016 - full year data expected | 219.5 | 54 | 95.74% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | CATTON LEA CSO | 6NW800884 | 232/1001 | 232/1001 |  | SO on sewer network | NY8291057410 | GB103023074710 | Allen from Source to West Allen | RIVER EAST ALLEN TRIBUTARY |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | 85 SNOWS GREEN ROAD CAULDWELL CSO | 6NW800951 | 234/1087 | 234/1087 |  | SO on sewer network | NZ0968053110 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | SNOWS GREEN BURN |  |  | Commissioned pre-2016 - full year data expected | 4.5 | 7 | 99.99%
Northumbrian Water | CAUSEY STW | 6NW800748 | 235/2007 | 235/2007 | 235/2007-02 | Storm tank at WwTW | NZ2039056050 | GB103023075670 | Team from Source to Tyne | CAUSEY BURN |  |  | Commissioned in 2020 - full year data expected | 437.5992 | 27 | 100%
Northumbrian Water | CEMETERY RD SSO | 6NW801489 | 255/1057 | 255/1057 |  | SO on sewer network | NZ3775038875 | GB103025075930 | Castle Eden Burn from Source to North Sea | EDDERACRES BURN |  |  | Commissioned pre-2016 - full year data expected | 2.75 | 5 | 25.29% | Comms failure / issue | N/A - Ongoing investigation
Northumbrian Water | CEMETERY ROAD CSO | 6NW801435 | 235/C/0047 | 235/C/0047 |  | SO on sewer network | NZ3306464319 | GB103023075690 | Don from Source to Tidal Limit | DON |  |  | Commissioned pre-2016 - full year data expected | 66 | 19 | 50.55% | Comms failure / issue | Scheduled
Northumbrian Water | CHAPEL COURT DU068 | 6NW801653 | 245/1081 | 245/1081 |  | SO on sewer network | NZ3187241798 | GB103024077490 | Old Durham Beck from Source to Pittington Beck | SHERBURN HOUSE BECK |  |  | Commissioned pre-2016 - full year data expected | 255.75 | 40 | 50.01% | Comms failure / issue | Resolved - November | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution
Northumbrian Water | CHAPEL STREET CSO | 6NW801640 | #TBC | Permit Anomaly | To be permitted for storm | SO on sewer network | NZ1946734630 | GB103024077464 | Wear from Gaunless to Browney | Willington Burn |  |  | Commissioned pre-2016 - full year data expected | 2.5 | 6 | 99.99%
Northumbrian Water | CHAPEL STREET CSO | 6NW801075 | 243/0931 | 243/0931 |  | SO on sewer network | NZ2037430858 | GB103024077464 | Wear from Gaunless to Browney | WEAR TRIB |  |  | Commissioned pre-2016 - full year data expected | 2.5 | 7 | 99.78%
Northumbrian Water | CHARE BANK CSO | 6NW800958 | 234/1156 | 234/1156 |  | SO on sewer network | NZ1005055440 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | RIVER DERWENT |  |  | Commissioned pre-2016 - full year data expected | 123 | 33 | 96.08%
Northumbrian Water | CHARLAW TERRACE CSO | 6NW800296 | 245/1071 | 245/1071 |  | SO on sewer network | NZ2358647845 | GB103024077623 | South Burn to confluence with Wear | CULVERTED WATERC' TO BLACK BUR |  |  | Commissioned in 2017 - full year data expected | 0.6 | 14 | 64.73% | Comms failure / issue | Scheduled
Northumbrian Water | CHARLTON VILLAGE 1 SSO | 6NW801617 | 25/06/1026 | 25/06/1026 |  | SO on sewer network | NZ6490015850 | GB103025071970 | Skelton Beck Catch (Saltburn) trib of North Sea | LITTLE BECK (SKELTON CATCHMEN) |  |  | Commissioned pre-2016 - full year data expected | 0.5 | 2 | 99.98%
Northumbrian Water | CHATTON CSO | 6NW800214 | NPSWQD006661 | NPSWQD006661 |  | SO on sewer network | NU0614028346 | GB102021073042 | Till from Roddam Burn to Glen | THE RIVER TILL |  |  | Commissioned in 2018 - full year data expected | 102 | 8 | 21.32% | Comms failure / issue | Resolved - November
Northumbrian Water | CHATTON STW | 6NW800688 | 210/0328 | Permit Anomaly - STW permit 210/0328 | To be permitted for storm | Inlet SO at WwTW | NU0597728706 | GB102021073042 | Till from Roddam Burn to Glen | River Till |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | CHERRY BANKS CSO | 6NW801283 | 245/1306 | 245/1306 |  | SO on sewer network | NZ2823452408 | GB103024077624 | Wear DS of Lumley Park Burn to Tidal Limit | WEAR TRIBUTARY |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | CHESTER LE STREET STW STORM TANK | 6NW800768 | 245/1242 | 245/1242 | A2 | Storm tank at WwTW | NZ2805051740 | GB103024077624 | Wear DS of Lumley Park Burn to Tidal Limit | WEAR |  |  | Commissioned in 2020 - full year data expected | 840.3072 | 68 | 100%
Northumbrian Water | CHESTER LE STREET STW CSO Inlet | 6NW800168 | 245/1242 | 245/1242 | A3 | Inlet SO at WwTW | NZ2805051740 | GB103024077624 | Wear DS of Lumley Park Burn to Tidal Limit | WEAR |  |  | Commissioned in 2019 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | CHILTON LANE A CSO | 6NW800445 | 253/1097 | QR.25/03/1097 |  | SO on sewer network | NZ3044931749 | GB103025072520 | Carrs from Source to Skerne | TRIB OF THE CARRS RVR SKERNE |  |  | Commissioned in 2016 - full year data expected | 230.5 | 29 | 96.64%
Northumbrian Water | CHILTON LANE B SSO | 6NW801358 | 253/1098 | QR.25/03/1098 |  | SO on sewer network | NZ3063431202 | GB103025072520 | Carrs from Source to Skerne | River Skerne |  |  | Commissioned pre-2016 - full year data expected | 202.25 | 56 | 99.7%
Northumbrian Water | CHILTON LANE PS | 6NW800567 | 253/1287 | 253/1287 | A1 | Storm discharge at pumping station | NZ3090030910 | GB103025072520 | Carrs from Source to Skerne | MAINSFORTH STELL (SKERNE) |  |  | Commissioned in 2019 - full year data expected | 1232.3014 | 86 | 94.46% |  |  | Performance - Infiltration
Northumbrian Water | CHOPWELL PARK FOOTPATH CSO | 6NW801635 | 234/1123 | 234/1123 |  | SO on sewer network | NZ1200258113 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | TONGUE BURN |  |  | Commissioned pre-2016 - full year data expected | 3.25 | 6 | 99.98%
Northumbrian Water | CHOPWELL ROAD CSO | 6NW800980 | 234/1139 | 234/1139 |  | SO on sewer network | NZ1215656843 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | RIVER DERWENT |  |  | Commissioned pre-2016 - full year data expected | 47.75 | 21 | 99.91%
Northumbrian Water | CHOWDENE CSO | 6NW801210 | 235/F/0655 | 235/F/0655 |  | SO on sewer network | NZ2580559497 | GB103023075670 | Team from Source to Tyne | TEAM, TRIBUTARY OF |  |  | Commissioned pre-2016 - full year data expected | 38.5 | 31 | 99.98%
Northumbrian Water | CHRISTON BANK SPS | 6NW800862 | 221/1030 | 221/1030 | 221/1030-01 | Storm discharge at pumping station | NU2101023300 | GB103022076400 | Brunton burn from Source to N Sea | UNNAMED TRIB OF BRUNTON BURN |  |  | Commissioned pre-2016 - full year data expected | 418.75 | 52 | 99.98%
Northumbrian Water | CHURCH BANK CSO | 6NW800363 | 235/1777 | 235/1777 |  | SO on sewer network | NZ3115466912 | GB103023075760 | Wallsend Burn (Trib of Tyne) | WALLSEND BURN SALINE ESTUARY |  |  | Commissioned in 2020 - full year data expected | 34.75 | 27 | 96.62%
Northumbrian Water | CHURCH DENE CSO | 6NW800886 | 232/1010 | 232/1010 |  | SO on sewer network | NY8385655983 | GB103023074710 | Allen from Source to West Allen | UNNAMED TRIB RIVER BURN |  |  | Commissioned pre-2016 - full year data expected | 62.5 | 25 | 96.03%
Northumbrian Water | CHURCH LANE HIGH STREET CSO | 6NW801596 | 254/1406 | 254/1406 |  | SO on sewer network | NZ5490718880 | 10 | #N/A | HOLME BECK |  |  | Commissioned pre-2016 - full year data expected | 16.75 | 14 | 99.99%
Northumbrian Water | CHURCH LANE CSO | 6NW801634 | 244/1023 | 244/1023 |  | SO on sewer network | NZ1226039080 | GB103024077270 | Deerness from Source to Hedleyhope Burn | DEERNESS |  |  | Commissioned pre-2016 - full year data expected | 14.75 | 13 | 99.68%
Northumbrian Water | CHURCH ROAD CSO | 6NW800947 | 234/1132 | 234/1132 |  | SO on sewer network | NZ0970051700 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | BACKSTONE BURN |  |  | Commissioned pre-2016 - full year data expected | 108.5 | 52 | 97.39%
Northumbrian Water | CHURCH STREET CSO | 6NW800819 | 210/1320 | 210/1320 |  | SO on sewer network | NT9941328257 | GB102021072930 | Wooler Water from Harthope Burn to Till | WOOLER WATER |  |  | Commissioned pre-2016 - full year data expected | 21.75 | 23 | 84.32% | Comms failure / issue | Resolved - October
Northumbrian Water | CHURCH STREET DU026 | 6NW801659 | 245/1388 | 245/1388 |  | SO on sewer network | NZ2743741803 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | RIVER WEAR |  |  | Commissioned pre-2016 - full year data expected | 2 | 6 | 99.94%
Northumbrian Water | CHURCH STREET NO26 CSO | 6NW801448 | NPSWQD008982 | NPSWQD008982 |  | SO on sewer network | NZ3304649836 | GB103024077580 | Lumley Park Burn from Source to Herrington Burn | MOORS BURN |  |  | Commissioned pre-2016 - full year data expected | 58.75 | 38 | 99.99%
Northumbrian Water | HIGH PITTINGTON STW CSO CHURCH VALE 1 | 6NW801232 | 245/E/0065 | 245/E/0065 |  | SO on sewer network | NZ3328043830 | GB103024077540 | Pittington Beck from Coalford to Old Durham Beck | COALFORD BECK |  |  | Commissioned pre-2016 - full year data expected | 1.5 | 3 | 99.47%
Northumbrian Water | HIGH PITTINGTON CSOS, MHS 27,28&29 COALFORD LANE Church Vale 2 | 6NW801664 | 245/1385 | 245/1385 |  | SO on sewer network | NZ3320043800 | GB103024077540 | Pittington Beck from Coalford to Old Durham Beck | COALFORD BECK |  |  | Commissioned pre-2016 - full year data expected | 1 | 3 | 99.99%
Northumbrian Water | CHURCH VILLAS CSO | 6NW801445 | 245/1260 | 245/1260 |  | SO on sewer network | NZ3415041150 | GB103024077490 | Old Durham Beck from Source to Pittington Beck | SHADFORTH BECK |  |  | Commissioned pre-2016 - full year data expected | 57 | 26 | 97.54%
Northumbrian Water | CLARA VALE SPS | 6NW800994 | 235/1743 | 235/1743 | A1 | Storm discharge at pumping station | NZ1305065100 | GB510302310200 | TYNE | RIVER TYNE SALINE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 386.5 | 45 | 65.61% | Comms failure / issue | N/A - Ongoing investigation
Northumbrian Water | CLEASEWELL HILL SPS | 6NW801220 | NPSWQD007427 | NPSWQD007427 | NPSWQD007427-01 | Storm discharge at pumping station | NZ2564785809 | GB103022077062 | Wansbeck from Bothal Burn to North Sea | WANSBECK (SALINE ESTUARY) |  |  | Commissioned pre-2016 - full year data expected | 181 | 44 | 98.95%
Northumbrian Water | CLEVLAND ROAD C.S.O. | 6NW801587 | 255/5016 | QC.25/05/5016 |  | SO on sewer network | NZ5113134233 | GB103025075880 | Hart Beck from Source to Sea (Hartlepool) | Culverted Watercourse into The Slake |  |  | Commissioned pre-2016 - full year data expected | 883.25 | 72 | 99.87% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | CLIFTON LODGE CSO | 6NW800428 | NPSWQD003961 | NPSWQD003961 |  | SO on sewer network | NZ4953431831 | 368 | #N/A | UNNAMED WATERCOURSE |  |  | June 2021 | 0.25 | 1 | 41.76% | Sensor failure / issue | Resolved - November
Northumbrian Water | CLOCKWOOD SEWAGE PUMPING STATION | 6NW800622 | 25/04/1679 | 25/04/1679 | 25/04/1679-03 | Storm discharge at pumping station | NZ4292012580 | GB103025072595 | Tees from Skerne to Tidal Limit | RIVER TEES |  |  | Commissioned pre-2016 - full year data expected | 481 | 52 | 99.75%
Northumbrian Water | CLOCKWOOD SEWAGE PUMPING STATION | 6NW800623 | 25/04/1679 | 25/04/1679 | 25/04/1679-01 | Storm discharge at pumping station | NZ4292012580 | GB103025072595 | Tees from Skerne to Tidal Limit | RIVER TEES |  |  | Commissioned in 2020 - full year data expected | 0.089722 | 3 | 100%
Northumbrian Water | CLOSE HOUSE STORM SEWAGE OVERFLOW | 6NW801156 | 242/1013 | 242/1013 |  | SO on sewer network | NZ2331027860 | GB103024072730 | Gaunless from Hummer Beck to Wear | DENE BECK |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 86.16% | Comms failure / issue | Scheduled
Northumbrian Water | HIGH PITTINGTON CSOS, MHS 27,28&29 COALFORD LANE | 6NW801422 | 245/1343 | 245/1343 |  | SO on sewer network | NZ3333943853 | GB103024077540 | Pittington Beck from Coalford to Old Durham Beck | Coalford Beck |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 96.14%
Northumbrian Water | WEST COATHAM LANE CSO | 6NW801601 | 254/1914 | 254/1914 |  | SO on sewer network | NZ5797023810 | GB103025072320 | Tees Estuary (S Bank) | TRIB OF THE FLEET |  |  | Commissioned pre-2016 - full year data expected | 29 | 9 | 99.39%
Northumbrian Water | COCHRANE STREET CSO | 6NW800257 | 233/1020 | 233/1020 |  | SO on sewer network | NZ1822463606 | GB510302310200 | TYNE | TYNE |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 100%
Northumbrian Water | BLACKBURN BRIDGE CSO (TE 015) | 6NW800989 | 242/1056 | 242/1056 |  | SO on sewer network | NZ1335024560 | GB103024072690 | Gaunless from Source to Hummer Beck | THE BLACK BURN |  |  | Commissioned pre-2016 - full year data expected | 10.25 | 14 | 92.88%
Northumbrian Water | COCKFIELD FELL NO2 CSO | 6NW800988 | 242/1054 | 242/1054 |  | SO on sewer network | NZ1332024630 | GB103024072690 | Gaunless from Source to Hummer Beck | THE BLACK BURN VIA A SW SEWER |  |  | Commissioned pre-2016 - full year data expected | 0.5 | 2 | 83.57% | Sensor failure / issue | Scheduled
Northumbrian Water | COCKFIELD STW | 6NW800726 | 242/1052 | 242/1052 | A2 | Storm tank at WwTW | NZ1363224900 | GB103024072690 | Gaunless from Source to Hummer Beck | GAUNLESS |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | COLDWELL BURN SSO | 6NW801494 | 245/0264 | 245/0264 |  | SO on sewer network | NZ3802044140 | GB103024077540 | Pittington Beck from Coalford to Old Durham Beck | COLDWELL BURN |  |  | Commissioned pre-2016 - full year data expected | 0.25 | 1 | 99.99%
Northumbrian Water | COLWELL STW | 6NW801681 | 231/1077 | 231/1077 | 231/1077-03 | Inlet SO at WwTW | NY9538075020 | GB103023074890 | Barrasford Burn Catchment (trib of N Tyne) | COAL BURN |  |  | Commissioned in 2020 - full year data expected | 3136.2681 | 148 | 100%
Northumbrian Water | COLWELL STW CSO Inlet | 6NW800139 | 231/1077 | 231/1077 | 231/1077-04 | Inlet SO at WwTW | NY9538075020 | GB103023074890 | Barrasford Burn Catchment (trib of N Tyne) | COAL BURN |  |  | Commissioned in 2020 - full year data expected | 436.1181 | 35 | 82.76% | Installation set-up/design issue | Resolved - April
Northumbrian Water | CONE LANE (CHESTER NO 4) CSO | 6NW801665 | 245/1328 | 245/1328 |  | SO on sewer network | NZ2744951601 | GB103024077600 | Cong Burn from Twizell Burn to Wear | CHESTER BURN |  |  | Commissioned pre-2016 - full year data expected | 3.5 | 7 | 98.81%
Northumbrian Water | CONGBURN BANK CSO | 6NW801161 | 245/E/0621 | 245/E/0621 |  | SO on sewer network | NZ2354749568 | GB103024077560 | Cong Burn from Source to Twizell Burn | CONG BURN |  |  | Commissioned pre-2016 - full year data expected | 2 | 6 | 99.95%
Northumbrian Water | CONISCLIFFE ROAD CSO | 6NW801570 | 25/05/5029 | 25/05/5029 |  | SO on sewer network | NZ4873432427 | 368 | #N/A | BURN VALLEY BECK |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | CONISHEAD TERRACEM SOUTH HETTON CSO | 6NW801490 | 245/A/0605 | 245/A/0605 |  | SO on sewer network | NZ3759145674 | GB103024077540 | Pittington Beck from Coalford to Old Durham Beck | COLDWELL BURN, TRIBUTARY OF |  |  | Commissioned pre-2016 - full year data expected | 233.75 | 44 | 99.96%
Northumbrian Water | CONSETT ACADEMY SOUTH CSO DER090 | 6NW800941 | 234/1154 | 234/1154 |  | SO on sewer network | NZ0844449648 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | UNNAMED TRIB OF DENE BURN |  |  | Commissioned pre-2016 - full year data expected | 66.25 | 34 | 84.95% | Sensor failure / issue | Resolved - November
Northumbrian Water | FELLSIDE CSO (DER 174) | 6NW800974 | 244/1010 | 244/1010 |  | SO on sewer network | NZ1143049200 | GB103024077330 | Smallhope Burn from Source to Browney, Stocke | BACKGILL BURN TRIBUTARY |  |  | Commissioned pre-2016 - full year data expected | 22 | 19 | 99.98%
Northumbrian Water | CONSETT OAP HALL CSO | 6NW800946 | EPRAB3596NY | EPRAB3596NY |  | SO on sewer network | NZ0894552307 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | BACKSTONE BURN |  |  | Commissioned pre-2016 - full year data expected | 1 | 3 | 94.55%
Northumbrian Water | CONSETT STW | 6NW800717 | 234/1061 | 234/1061 | 234/1061-02 | Storm tank at WwTW | NZ0940255072 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | RIVER DERWENT |  |  | Commissioned in 2020 - full year data expected | 1273.9411 | 155 | 100%
Northumbrian Water | COOPERS CLOSE CSO | 6NW800388 | 255/1195 | 255/1195 |  | SO on sewer network | NZ3667039970 | GB103025075930 | Castle Eden Burn from Source to North Sea | TRIB. OF GORE BURN |  |  | Commissioned pre-2016 - full year data expected | 0.25 | 1 | 99.99%
Northumbrian Water | COPELAND ESTATE OFF SITE SEWER | 6NW801041 | 242/E/0382 | 242/E/0382 |  | SO on sewer network | NZ1787625987 | GB103024072690 | Gaunless from Source to Hummer Beck | GAUNLESS |  |  | Commissioned pre-2016 - full year data expected | 2 | 5 | 96.46%
Northumbrian Water | CORMORANT DRIVE CSO | 6NW801165 | 235/1887 | 235/1887 |  | SO on sewer network | NZ2328162557 | GB510302310200 | TYNE | RIVER TEAM SALINE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 717.1 | 133 | 99.58%
Northumbrian Water | CORNFIELD ROAD PUMPING STATION | 6NW800629 | 254/1805 | 254/1805 | 254/1805-01 | Storm discharge at pumping station | NZ4475617659 | GB103025072595 | Tees from Skerne to Tidal Limit | TEES ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 0.25 | 1 | 94.8%
Northumbrian Water | COXHOE CSO CORNFORTH LANE | 6NW801380 | 243/0986 | 243/0986 |  | SO on sewer network | NZ3170034920 | GB103024077410 | Croxdale Beck from Source to Wear | COXHOE BECK |  |  | Commissioned pre-2016 - full year data expected | 3.75 | 8 | 99.73%
Northumbrian Water | CORNHILL SPS | 6NW800454 | 210/0984 | 210/0984 | A1 | Storm discharge at pumping station | NT8615039400 | GB102021073010 | Willow Burn Catchment (Trib of Tweed) | CORNHILL MILL BURN |  |  | Commissioned in 2020 - full year data expected | 0.031667 | 1 | 36.51% | Comms failure / issue | Resolved - August
Northumbrian Water | CORONATION ST CSO | 6NW800390 | EPRBP3720XY | EPRBP3720XY |  | SO on sewer network | NZ3583766907 | 8 | #N/A | RIVER TYNE (ESTUARY) |  |  | Commissioned in 2018 - full year data expected | 259.9267 | 40 | 100%
Northumbrian Water | COTHERSTONE SEWAGE TREATMENT WORKS | 6NW800143 | 25/01/0920 | 25/01/0920 | A2 | Inlet SO at WwTW | NZ0071020010 | GB103025072240 | Balder Catchment (trib of Tees) | RIVER BALDER |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | COTSFORD JUNIOR SCHOOL CSO | 6NW801553 | 255/1212 | 255/1212 |  | SO on sewer network | NZ4466041300 | 367 | #N/A | BLACKHILLS GILL |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | COW PLANTATION CSO | 6NW801196 | 243/0973 | 243/0973 |  | SO on sewer network | NZ2558834626 | GB103024077350 | Valley Burn from Source to Wear | VALLEY BURN, RIVER WEAR |  |  | Commissioned pre-2016 - full year data expected | 25.75 | 23 | 94.63%
Northumbrian Water | COWPEN BEWLEY SPS | 6NW800643 | 25/04/1785 | 25/04/1785 | A1 | Storm discharge at pumping station | NZ4778725271 | GB103025072380 | Cowbridge Beck from Source to North Burn | TRIB OF COWBRIDGE BECK |  |  | Commissioned pre-2016 - full year data expected | 463.5 | 43 | 94.21%
Northumbrian Water | COWPEN ROAD CSO | 6NW801352 | EPRJB3399NK | EPRJB3399NK |  | SO on sewer network | NZ2960382326 | 5 | #N/A | RIVER BLYTH |  |  | Commissioned pre-2016 - full year data expected | 4 | 11 | 99.96%
Northumbrian Water | COX GREEN PUMPING STATION | 6NW800584 | 245/1218 | 245/1218 | A1 | Storm discharge at pumping station | NZ3270055320 | GB510302402900 | WEAR | RIVER WEAR (SALINE ESTUARY) |  |  | Commissioned in 2020 - full year data expected | 153.4428 | 10 | 100%
Northumbrian Water | KIMBERLEY GARDENS CSO (DER 82) | 6NW000001 | 245/1308 | 245/1308 |  | SO on sewer network | NZ2123051430 | GB103024077590 | Twizell Burn from Source to Cong Burn | TWIZELL BURN TRIBUTARY |  |  | Commissioned pre-2016 - full year data expected | 182.75 | 50 | 96.28%
Northumbrian Water | FRONT STREET CSO | 6NW000002 | 245/1331 | 245/1331 |  | SO on sewer network | NZ2141051180 | GB103024077590 | Twizell Burn from Source to Cong Burn | STANLEY BURN TRIBUTARY |  |  | Commissioned pre-2016 - full year data expected | 4.25 | 6 | 99.99%
Northumbrian Water | CRAMLINGTON SEWAGE TREATMENT WORKS CSO INLET | 6NW800166 | 226/1187 | 226/1187 | 226/1187-03 | Inlet SO at WwTW | NZ2952082460 | GB510302203200 | BLYTH (N) | RIVER BLYTH (SALINE ESTUARY) |  |  | Commissioned in 2020 - full year data expected | 329.2128 | 43 | 100%
Northumbrian Water | CRAMLINGTON SEWAGE TREATMENT WORKS Storm Tank | 6NW800765 | 226/1187 | 226/1187 | 226/1187-04 | Storm tank at WwTW | NZ2952082460 | GB510302203200 | BLYTH (N) | RIVER BLYTH (SALINE ESTUARY) |  |  | Commissioned in 2020 - full year data expected | 97.5 | 12 | 50.05% | Installation set-up/design issue | Resolved - July
Northumbrian Water | CRASTER NORTH SPS | 6NW800480 | 221/0921 | 221/0921 | A1 | Storm discharge at pumping station | NU2590020080 | GB650301500001 | Northumberland South | NORTH SEA |  |  | Commissioned in 2020 - full year data expected | 119.1556 | 49 | 99.3%
Northumbrian Water | CRASTER SOUTH SPS | 6NW800478 | 221/0920 | 221/0920 | A1 | Storm discharge at pumping station | NU2600019500 | GB650301500001 | Northumberland South | NORTH SEA |  |  | Commissioned in 2020 - full year data expected | 160.9892 | 92 | 100%
Northumbrian Water | CSO AT CRATHORNE PUMPING STATION | 6NW800628 | QR.25/04/1582 | QR.25/04/1582 | S1 | Storm discharge at pumping station | NZ4416007540 | GB103025071880 | Leven from Tame to River Tees | THE RIVER LEVEN |  |  | Commissioned in 2020 - full year data expected | 722.8178 | 78 | 100%
Northumbrian Water | CREE BECK CSO | 6NW801355 | NPSWQD005054 | NPSWQD005054 |  | SO on sewer network | NZ3065712805 | GB103025072160 | Neasham Stell Catchment (trib of Tees) | CREE BECK |  |  | Commissioned pre-2016 - full year data expected | 3.25 | 4 | 99.98%
Northumbrian Water | CRESSWELL SEWAGE PUMPING STATION | 6NW800566 | 224/0986 | 224/0986 | A1 | Storm discharge at pumping station | NZ2978193771 | GB650301500001 | Northumberland South | NORTH SEA |  |  | Commissioned in 2018 - full year data expected | 43.7522 | 9 | 99.79%
Northumbrian Water | CRICKET GROUND HOLMSIDE LANE CSO | 6NW801083 | EPRBB3496RP | EPRBB3496RP |  | SO on sewer network | NZ1906848156 | GB103024077560 | Cong Burn from Source to Twizell Burn | TRIBUTARY OF IDDESTON'S SIKE |  |  | Commissioned pre-2016 - full year data expected | 1.75 | 4 | 85.71% | Comms failure / issue | Resolved - October
Northumbrian Water | CRIMDON PARK PUMPING STATION | 6NW800645 | 255/1115 | 255/1115 | 255/1115-3A (Storm Sewage) | Storm discharge at pumping station | NZ4841036730 | GB103025075910 | Crimdon Beck from Source to Sea | NORTH SEA |  | Crimdon | Commissioned pre-2016 - full year data expected | 75.4667 | 13 | 81.38% | Comms failure / issue | Resolved - November
Northumbrian Water | CROFT PS | 6NW800557 | 254/1018 | 254/1018 | A | Storm discharge at pumping station | NZ2898009210 | GB103025072030 | Spa Beck Catchment (trib of Tees) | SPA BECK (TEES) |  |  | Commissioned in 2020 - full year data expected | 622.7944 | 47 | 97.97%
Northumbrian Water | CROFTDALE ROAD CSO | 6NW801058 | 235/1437 | 235/1437 |  | SO on sewer network | NZ1822463606 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 16.4333 | 21 | 99.91%
Northumbrian Water | CROOKHALL STW CSO INLET | 6NW800150 | 244/1006 | 244/1006 | 244/1006-03 | Inlet SO at WwTW | NZ1256050430 | GB103024077330 | Smallhope Burn from Source to Browney, Stocke | STOCKERLEY BURN, TRIBUTARY OF |  |  | Commissioned in 2020 - full year data expected | 359.1731 | 80 | 99.84%
Northumbrian Water | CROOKHALL STW Storm Tank | 6NW800724 | 244/1006 | 244/1006 | 244/1006-02 | Storm tank at WwTW | NZ1256050430 | GB103024077330 | Smallhope Burn from Source to Browney, Stocke | STOCKERLEY BURN, TRIBUTARY OF |  |  | Feb 2021 | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | CROOKHAM STW | 6NW800103 | 210/0115 | Permit Anomaly - STW permit 210/0115 | To be permitted for storm | Inlet SO at WwTW | NT9190038200 | GB102021073050 | Till from Glen to River Tweed | River Till |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | CROSS LANE CSO CH8 | 6NW800303 | 245/1283 | 245/1283 |  | SO on sewer network | NZ2445747784 | GB103024077623 | South Burn to confluence with Wear | BLACK BURN RIVER WEAR |  |  | Commissioned pre-2016 - full year data expected | 2 | 1 | 73.54% | Comms failure / issue | Resolved - March
Northumbrian Water | CROSS STREET CSO | 6NW801227 | 243/0916 | 243/0916 |  | SO on sewer network | NZ2654837751 | GB103024077464 | Wear from Gaunless to Browney | WEAR |  |  | Commissioned pre-2016 - full year data expected | 0.75 | 3 | 99.99%
Northumbrian Water | CROSSFELL SEWAGE PUMPING STATION | 6NW801014 | 226/A/0973 | 226/A/0973 | 226/A/0973 (Storm Sewage) | Storm discharge at pumping station | NZ1553071670 | GB103022076860 | Pont from Med Burn to Small Burn | PONT, TRIBUTARY OF |  |  | Commissioned pre-2016 - full year data expected | 4 | 1 | 97.88%
Northumbrian Water | CSO WV80 DISUSED STW HUNWICK | 6NW801077 | 243/0910 | 243/0910 |  | SO on sewer network | NZ2000633593 | GB103024077464 | Wear from Gaunless to Browney | WEAR |  |  | Commissioned pre-2016 - full year data expected | 35.5 | 8 | 5.671% | Comms failure / issue | Resolved - December | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | CSO 200M WEST OF WALTON ROAD | 6NW801414 | 245/1152 | 245/1152 |  | SO on sewer network | NZ3349556008 | GB510302402900 | WEAR | WEAR TRIB |  |  | Commissioned pre-2016 - full year data expected | 2.8333 | 2 | 100%
Northumbrian Water | CSO 32 WALBOTTLE ROAD | 6NW801032 | 235/1876 | 235/1876 |  | SO on sewer network | NZ1693265809 | GB103023075740 | New Burn (Trib of Tyne) | NEW BURN |  |  | Commissioned pre-2016 - full year data expected | 5.8 | 6 | 100%
Northumbrian Water | CSO ADJACENT 40 HOLLYHILL GARDENS | 6NW801088 | 245/1258 | 245/1258 |  | SO on sewer network | NZ1995851833 | GB103024077590 | Twizell Burn from Source to Cong Burn | TRIB OF STANLEY BURN |  |  | Commissioned pre-2016 - full year data expected | 73.5 | 38 | 99.69%
Northumbrian Water | CSO AT CHURCH DENE | 6NW801010 | 233/1004 | 233/1004 |  | SO on sewer network | NZ1503665089 | GB510302310200 | TYNE | RIVER TYNE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 9.5 | 8 | 51.09% | Comms failure / issue | Resolved - July
Northumbrian Water | CSO AT CROMWELL ROAD | 6NW800349 | 235/1199 | 235/1199 |  | SO on sewer network | NZ2966463002 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | Commissioned in 2018 - full year data expected | 44.5511 | 27 | 100%
Northumbrian Water | CSO AT GREEN LANE | 6NW801557 | 254/1174 | 254/1174 |  | SO on sewer network | NZ4481816925 | GB103025072595 | Tees from Skerne to Tidal Limit | TEES |  |  | Commissioned pre-2016 - full year data expected | 89.2 | 47 | 100%
Northumbrian Water | CSO AT SW CORNER OF ALLOTMENT GARDEN HEBBURN Riverside | 6NW800355 | 235/1187 | 235/1187 |  | SO on sewer network | NZ2996963711 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | Commissioned in 2019 - full year data expected | 16 | 8 | 99.71%
Northumbrian Water | HEUGH ROAD PUMPING STATION | 6NW800479 | 221/0918 | 221/0918 | A | Storm discharge at pumping station | NU2593019820 | GB650301500001 | Northumberland South | NORTH SEA |  |  | Commissioned in 2020 - full year data expected | 93.9658 | 15 | 100%
Northumbrian Water | HEWORTH SHORE CSO | 6NW801315 | 235/1201 | 235/1201 |  | SO on sewer network | NZ2872062720 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 29.25 | 9 | 99.99%
Northumbrian Water | JANADAB CSO | 6NW800347 | 235/1200 | 235/1200 |  | SO on sewer network | NZ2903062876 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | Commissioned in 2020 - full year data expected | 7.75 | 15 | 82.07% | Comms failure / issue | Resolved - March
Northumbrian Water | CSO AT MANHOLE 49 HOWDEN ROAD | 6NW800376 | 235/1489 | 235/1489 |  | SO on sewer network | NZ3496266848 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | Commissioned in 2017 - full year data expected | 0 | 0 | 94.87%
Northumbrian Water | NEST ROAD CSO | 6NW801288 | 235/1203 | 235/1203 |  | SO on sewer network | NZ2824063000 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 0.25 | 1 | 99.98%
Northumbrian Water | PRESTON LANE CSO | 6NW801536 | 254/1177 | 254/1177 |  | SO on sewer network | NZ4327215893 | GB103025072595 | Tees from Skerne to Tidal Limit | TEES ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 100%
Northumbrian Water | CSO AT REAR OF ORCHID CRESCENT | 6NW801287 | 235/1204 | 235/1204 |  | SO on sewer network | NZ2787463271 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | Commissioned in 2018 - full year data expected | 324.9197 | 48 | 100%
Northumbrian Water | REYROLLE SEWER (NORTH) CSO | 6NW800357 | 235/1185 | 235/1185 |  | SO on sewer network | NZ3004064490 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | EDM to be installed by December 2023 | #N/A | #N/A | #N/A
Northumbrian Water | ST PETERS PUMPING STATION OUTFALL N | 6NW800618 | 245/1004 | 245/1004 | A1 | Storm discharge at pumping station | NZ4011057550 | GB510302402900 | WEAR | WEAR ESTUARY |  |  | Commissioned in 2020 - full year data expected | 416.3581 | 38 | 100%
Northumbrian Water | STAITHES ROAD CSO | 6NW800297 | 235/1253 | 235/1253 |  | SO on sewer network | NZ2325962470 | GB510302310200 | TYNE | RIVER TEAM |  |  | Commissioned in 2019 - full year data expected | 335.3022 | 52 | 99.99%
Northumbrian Water | STATION STREET CSO | 6NW801558 | 254/1277 | 254/1277 |  | SO on sewer network | NZ4496718363 | GB103025072595 | Tees from Skerne to Tidal Limit | TEES ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 15.1 | 27 | 87.47% | Comms failure / issue | Scheduled
Northumbrian Water | CSO AT STONEYGATE LANE | 6NW801314 | 235/1202 | 235/1202 |  | SO on sewer network | NZ2868262713 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 3.0333 | 6 | 100%
Northumbrian Water | SUN STREET STORM SEWAGE OVERFLOW | 6NW800419M2 | 254/1278 | 254/1278 | A1 | SO on sewer network | NZ4474017750 | GB103025072595 | Tees from Skerne to Tidal Limit | TEES ESTUARY |  |  | Commissioned in 2017 - full year data expected | 28.75 | 23 | 99.64%
Northumbrian Water | SUN STREET STORM SEWAGE OVERFLOW | 6NW800419M3 | 254/1278 | 254/1278 | A1 | SO on sewer network | NZ4474017750 | GB103025072595 | Tees from Skerne to Tidal Limit | TEES ESTUARY |  |  | Commissioned in 2017 - full year data expected | 53.75 | 30 | 98.56%
Northumbrian Water | CSO AT TEAM STREET | 6NW800299 | 235/1250 | 235/1250 |  | SO on sewer network | NZ2350062335 | GB510302310200 | TYNE | RIVER TEAM (ESTUARY) |  |  | Commissioned in 2018 - full year data expected | 356.6375 | 28 | 99.99%
Northumbrian Water | SWARLAND HOUSE SPS | 6NW800481 | 223/0864 | 223/0864 | A1 | Storm discharge at pumping station | NU2616004550 | GB510302203000 | COQUET | Guilders Burn |  | Warkworth & Amble Links | Commissioned in 2018 - full year data expected | 38.1739 | 10 | 100%
Northumbrian Water | SSO AT WEST END | 6NW800823 | 210/0939 | 210/0939 |  | SO on sewer network | NT9945052750 | GB510202110000 | TWEED | TWEED ESTUARY |  | Spittal | Commissioned pre-2016 - full year data expected | 16.3 | 17 | 100%
Northumbrian Water | BENTON WAY OUTFALL NO 2 CSO | 6NW801372 | 235/1626 | 235/1626 |  | SO on sewer network | NZ3013065600 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 4.25 | 6 | 99.77%
Northumbrian Water | BLACKHILLS FARM CSO | 6NW801554 | 255/1151 | 255/1151 |  | SO on sewer network | NZ4465641299 | 367 | #N/A | BLACKHILLS GILL |  |  | Commissioned pre-2016 - full year data expected | 8.25 | 9 | 99.99%
Northumbrian Water | CANTEBURY ROAD CSO | 6NW801275 | 245/1154 | 245/1154 |  | SO on sewer network | NZ2805044540 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | WEAR TRIB |  |  | Commissioned pre-2016 - full year data expected | 35.5 | 24 | 99.98%
Northumbrian Water | SALTBURN ATTENUATION TANK NO1 CARAVAN PARK | 6NW800442 | 25/06/0983 | 25/06/0983 |  | SO on sewer network | NZ6575021640 | 369 | #N/A | PIT HILLS STELL NORTH SEA |  | Saltburn Pier | Commissioned in 2018 - full year data expected | 351.4589 | 21 | 99.99%
Northumbrian Water | CLUMBER STREET CSO | 6NW800301 | 235/1318 | 235/1318 |  | SO on sewer network | NZ2322062910 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | Commissioned in 2019 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | COOP HOUSE WOOD CSO | 6NW801498 | 255/1135 | 255/1135 |  | SO on sewer network | NZ3935245268 | GB103025075970 | Dalton Beck to North Sea | COOP HOUSE DENE BURN |  | Seaham Beach | Commissioned pre-2016 - full year data expected | 552.9667 | 69 | 100%
Northumbrian Water | COTTAGE HOSPITAL CSO | 6NW801623 | 256/0939 | QR.25/06/0939 |  | SO on sewer network | NZ7003019636 | 369 | #N/A | UNNAMED TRIB OF UNNAMED POND |  |  | Commissioned pre-2016 - full year data expected | 1.5 | 6 | 99.99%
Northumbrian Water | DRAGON LANE CSO | 6NW801338 | 245/1136 | 245/1136 |  | SO on sewer network | NZ3107842600 | GB103024077540 | Pittington Beck from Coalford to Old Durham Beck | PITTINGTON BECK TRIB |  |  | Commissioned pre-2016 - full year data expected | 0.5 | 2 | 99.99%
Northumbrian Water | CSO DUNN STREET | 6NW801167 | 235/1631 | 235/1631 |  | SO on sewer network | NZ2382462901 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | #N/A | #N/A | 0% | Comms failure / issue | Scheduled
Northumbrian Water | EAST HOLBORN EAST CSO | 6NW801475 | 235/1645 | 235/1645 |  | SO on sewer network | NZ3567066620 | GB510302310200 | TYNE | TYNE SALINE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 28.54% | No longer operational as an overflow - permit revoked or to be revoked | N/A - Ongoing investigation
Northumbrian Water | CSO AT EAST HOLBORN WEST | 6NW801474 | 235/1644 | 235/1644 |  | SO on sewer network | NZ3567066623 | GB510302310200 | TYNE | RIVER TYEN ESTUARINE WATERS |  |  | Commissioned pre-2016 - full year data expected | 790.5278 | 34 | 28.51% | No longer operational as an overflow - permit revoked or to be revoked | N/A - Ongoing investigation
Northumbrian Water | BRANDON VILLAGE SSO STOBBS HOUSE | 6NW801157 | 244/0952 | 244/0952 |  | SO on sewer network | NZ2333040310 | GB103024077280 | Deerness from Hedleyhope Burn to Browney | DEERNESS TRIB |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | FALLSWAY CSO (DU57) | 6NW801362 | 245/1160 | 245/1160 |  | SO on sewer network | NZ3076044630 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | WEAR TRIB |  |  | Commissioned pre-2016 - full year data expected | 1.25 | 2 | 99.76%
Northumbrian Water | CSO FORTH BANKS | 6NW801186 | 235/1628 | 235/1628 |  | SO on sewer network | NZ2474263431 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 74.0667 | 36 | 100%
Northumbrian Water | GRANGETOWN CSO | 6NW800412 | 255/1202 | 255/1202 |  | SO on sewer network | NZ4130055290 | 367 | #N/A | WEAR ESTUARY |  |  | Commissioned in 2020 - full year data expected | 115.1078 | 30 | 100%
Northumbrian Water | CSO AT HILLIERSON TERRACE | 6NW800219 | 232/1022 | 232/1022 |  | SO on sewer network | NY7794943799 | GB103023075420 | Nent from Source to South Tyne | RIVER NENT |  |  | Commissioned in 2017 - full year data expected | 0.75 | 3 | 42.72% | Telemetry or data archiving failure / issue | Resolved - October
Northumbrian Water | HOLMSFOOT CSO | 6NW800883 | 232/1021 | 232/1021 |  | SO on sewer network | NY7784743968 | GB103023075420 | Nent from Source to South Tyne | RIVER NENT |  |  | Commissioned pre-2016 - full year data expected | 4.75 | 6 | 99.97%
Northumbrian Water | HORDEN BURN CSO NO.3 | 6NW801547 | 255/1152 | 255/1152 |  | SO on sewer network | NZ4467843637 | 367 | #N/A | North Sea |  |  | Commissioned pre-2016 - full year data expected | 1.5 | 2 | 99.69%
Northumbrian Water | JUNCTION LANGHOLME AVENUE & | 6NW801483 | 235/1590 | 235/1590 |  | SO on sewer network | NZ3620661987 | GB103023075690 | Don from Source to Tidal Limit | DON |  |  | Commissioned pre-2016 - full year data expected | 33 | 11 | 91.32%
Northumbrian Water | GARRIGILL MANHOLE 9901 SSO | 6NW800218 | 232/1020 | 232/1020 |  | SO on sewer network | NY7390641881 | GB103023075400 | South Tyne from Cross Gill to Black Burn (Aleson) | SOUTH TYNE |  |  | Commissioned in 2020 - full year data expected | 2.25 | 2 | 56.86% | Access - Unable to retrieve data from non-telemetry data logger (NB: not to be used for delayed access to fix existing fault) | Scheduled
Northumbrian Water | MICHEL BEARINGS NORTH CSO | 6NW800282 | 235/1671 | 235/1671 |  | SO on sewer network | NZ2123963426 | GB510302310200 | TYNE | RIVER TYNE |  |  | Commissioned in 2017 - full year data expected | 0 | 0 | 99.95%
Northumbrian Water | CSO NEPTUNE YARD NO.1 OUTFALL | 6NW800353 | 235/1623 | 235/1623 |  | SO on sewer network | NZ2997665306 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | Commissioned in 2018 - full year data expected | 18.3906 | 10 | 92.31%
Northumbrian Water | CSO NEW DRIVE RECREATION GROUND | 6NW801522 | 255/1154 | 255/1154 |  | SO on sewer network | NZ4169950096 | 367 | #N/A | ICE HOUSE DEAN |  | Seaham Hall | Commissioned pre-2016 - full year data expected | 0.63333 | 3 | 98.37%
Northumbrian Water | CSO ON WHICKHAM AND GATESHEAD SEWER | 6NW800298 | 235/1252 | 235/1252 |  | SO on sewer network | NZ2340862006 | GB510302310200 | TYNE | TEAM |  |  | Commissioned in 2018 - full year data expected | 362.0758 | 59 | 99.99%
Northumbrian Water | CSO OUTSIDE MILKWELL COTTAGES | 6NW800917 | 233/1246 | 233/1246 |  | SO on sewer network | NY9892964220 | GB103023075801 | Tyne from Watersmeet to Tidal Limit | RIVER TYNE |  |  | Commissioned pre-2016 - full year data expected | 0.5 | 2 | 99.98%
Northumbrian Water | CSO REAR 11 ST AUSTELL GARDENS | 6NW800313 | 235/1483 | 235/1483 |  | SO on sewer network | NZ2543758543 | GB103023075670 | Team from Source to Tyne | RIVER TEAM TRIBUTARY |  |  | Commissioned in 2017 - full year data expected | 1 | 1 | 98.64%
Northumbrian Water | REAR AGED MINERS HOMES CSO | 6NW800248 | 244/0916 | 244/0916 |  | SO on sewer network | NZ1828844481 | GB103024077551 | Browney from Smallhope Burn Deerness confl | HAMSTEELS BECK (RIVER BROWNEY) |  |  | Commissioned in 2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | CSO AT REAR OF HOLLY HOUSE | 6NW800429 | 25/05/5038 | 25/05/5038 |  | SO on sewer network | NZ4916032011 | 368 | #N/A | STREAM TRIB OF HARTLEPOOL BAY |  |  | Commissioned in 2017 - full year data expected | 0.5 | 1 | 99.99%
Northumbrian Water | CSO REDHEUGH BRIDGE | 6NW801185 | 235/1627 | 235/1627 |  | SO on sewer network | NZ2440963160 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 54.9333 | 43 | 99.94% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | RIVERSIDE PARK WEST CSO | 6NW801289 | 235/1765 | 235/1765 |  | SO on sewer network | NZ2788063420 | GB510302310200 | TYNE | RIVER TYNE SALINE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 1 | 2 | 99.99%
Northumbrian Water | CSO SALTERFEN SU47 | 6NW801523 | 255/1201 | 255/1201 |  | SO on sewer network | NZ4149653876 | GB650301500002 | Tyne and Wear | NORTH SEA |  |  | Commissioned pre-2016 - full year data expected | 74.25 | 22 | 24.16% | Comms failure / issue | N/A - Ongoing investigation
Northumbrian Water | MILL INN A SSO SEAHAM PARK | 6NW801510 | 255/1153 | 255/1153 |  | SO on sewer network | NZ4088049850 | 367 | #N/A | SEATON BURN |  | Seaham Hall | Commissioned pre-2016 - full year data expected | 0 | 0 | 100%
Northumbrian Water | SOUTH STREET STORM SEWAGE OVERFLOW SECOND STREET | 6NW800965 | 244/0956 | 244/0956 |  | SO on sewer network | NZ1214050620 | GB103024077330 | Smallhope Burn from Source to Browney, Stocke | STOCKERLEY BURN, TRIBUTARY OF |  |  | Commissioned pre-2016 - full year data expected | 4 | 11 | 91.09%
Northumbrian Water | CSO SKELTON (SALTBURN LANE) | 6NW800443 | 25/06/0986 | 25/06/0986 |  | SO on sewer network | NZ6671619795 | GB103025071960 | Saltburn Gill Catch trib of North Sea | TRIB OF SALTBURN GILL |  | Saltburn Pier | Commissioned in 2019 - full year data expected | 298.0764 | 32 | 100%
Northumbrian Water | CSO SUNDERLANS GAS WORKS | 6NW801524 | 255/1198 | 255/1198 |  | SO on sewer network | NZ4114055620 | GB650301500002 | Tyne and Wear | NORTH SEA |  |  | Commissioned pre-2016 - full year data expected | 21.25 | 13 | 99.99%
Northumbrian Water | SHERATON CSO 50M SW OF STW | 6NW801550 | 255/1132 | 255/1132 |  | SO on sewer network | NZ4416034790 | GB103025075910 | Crimdon Beck from Source to Sea | BELLOWS BURN |  |  | Commissioned pre-2016 - full year data expected | 9.75 | 10 | 99.99%
Northumbrian Water | CSO AT THREE MILE INN | 6NW801188 | 235/1725 | 235/1725 |  | SO on sewer network | NZ2432969572 | GB103023075780 | Ouse Burn from Source to Tyne | OUSE BURN |  |  | Commissioned pre-2016 - full year data expected | 4.75 | 3 | 99.99%
Northumbrian Water | CSO AT REAR OF 1 RIVER TERRACE | 6NW800225 | 25/01/0922 | 25/01/0922 |  | SO on sewer network | NY9487925005 | GB103025072511 | Tees from Maize Beck to Percy Beck | RIVER TEES |  |  | Commissioned in 2016 - full year data expected | 0 | 0 | 99.86%
Northumbrian Water | COS TO REAR 12 SPRINGWELL CLOSE | 6NW801040 | 25/02/1097 | 25/02/1097 |  | SO on sewer network | NZ1707220059 | GB103025072300 | Piercebridge Beck from Source to Tees | LANGTON BECK, TEES CATCH |  |  | Commissioned pre-2016 - full year data expected | 3 | 10 | 99.76%
Northumbrian Water | CSO TO REAR OF 8 OTTERINGTON CLOSE | 6NW801569 | 25/05/5039 | 25/05/5039 |  | SO on sewer network | NZ4723535060 | GB103025075880 | Hart Beck from Source to Sea (Hartlepool) | HART BECK |  |  | Commissioned pre-2016 - full year data expected | 54.25 | 24 | 99.83%
Northumbrian Water | CSO TO REAR NO.48 MARKET PLACE | 6NW800898 | 251/0924 | 251/0924 |  | SO on sewer network | NY9464525535 | GB103025072480 | Hudeshope Beck Catchment (trib of Tees) | Hudeshope Beck |  |  | Commissioned pre-2016 - full year data expected | 0.5 | 1 | 84.66% | Sensor failure / issue | Resolved - December
Northumbrian Water | CSO TO REAR OF 62 GRANGE AVE | 6NW801539 | QR.25/04/1563 | QR.25/04/1563 |  | SO on sewer network | NZ4305119456 | GB103025072550 | Lustrum Beck Catchment (trib of Tees) | UNNAMED TRIB OF LUSTRUM BECK |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 94%
Northumbrian Water | CSO AT WARKWORTH CRESCENT | 6NW801508 | 255/1157 | 255/1157 |  | SO on sewer network | NZ4042349383 | 367 | #N/A | SCAWPIE DEAN |  |  | Commissioned pre-2016 - full year data expected | 226.75 | 28 | 99.97%
Northumbrian Water | WARKWORTH DRIVE CSO | 6NW801234 | 245/1115 | 245/1115 |  | SO on sewer network | NZ2654049880 | GB103024077623 | South Burn to confluence with Wear | SOUTH BURN |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.24%
Northumbrian Water | CSO WATER STREET | 6NW801166 | 235/1632 | 235/1632 |  | SO on sewer network | NZ2361862898 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 149.6 | 45 | 100%
Northumbrian Water | CSO WELBECK ROAD & BATH STREET | 6NW801346 | 235/1331 | 235/1331 |  | SO on sewer network | NZ2984664771 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 114.7881 | 50 | 99.86%
Northumbrian Water | SIMONSIDE CSO WEST END | 6NW801440 | 226/1125 | 226/1125 |  | SO on sewer network | NZ3373775609 | GB103022076190 | Seaton Burn from Source to Tidal Limit | Seaton Burn |  | Seaton Sluice | Commissioned pre-2016 - full year data expected | 0.7 | 3 | 82.75% | Comms failure / issue | Resolved - December
Northumbrian Water | FISHBURN TCE SSO | 6NW801460 | 253/1100 | QR.25/03/1100 |  | SO on sewer network | NZ3561632005 | GB103025076070 | Skerne from Source to Carrs | Unnamed Tributary of the River Skerne |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | WEST LANE SCHOOL CSO | 6NW800237 | 234/0967 | 234/0967 |  | SO on sewer network | NZ1139056060 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | DERWENT TRIBUTARY |  |  | Commissioned in 2020 - full year data expected | 13.75 | 9 | 99.84%
Northumbrian Water | WHITTONSTALL CSO | 6NW800937 | 234/1026 | 234/1026 |  | SO on sewer network | NZ0776057870 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | MILL BURN |  |  | Commissioned pre-2016 - full year data expected | 0.25 | 1 | 96.49%
Northumbrian Water | CSO AT WOODLAND ROAD | 6NW800330 | 253/1099 | QR.25/03/1099 |  | SO on sewer network | NZ2750015334 | GB103025072596 | Skerne from Demons Beck to Tees | Cocker Beck |  |  | Commissioned in 2017 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | CSO YARM ROAD DL18 | 6NW801329 | 25/03/1214 | 25/03/1214 |  | SO on sewer network | NZ2912514232 | GB103025072596 | Skerne from Demons Beck to Tees | RIVER SKERNE |  |  | Commissioned pre-2016 - full year data expected | #N/A | #N/A | 0% | Comms failure / issue | Scheduled
Northumbrian Water | CUMBERLAND STREET SSO | 6NW801144 | 242/0641 | 242/0641 |  | SO on sewer network | NZ2244028130 | GB103024072730 | Gaunless from Hummer Beck to Wear | DENE BECK |  |  | Commissioned pre-2016 - full year data expected | 65.75 | 41 | 99.58%
Northumbrian Water | CUTLERS HALL ROAD (NO. 29) STORM | 6NW800232 | EPRAB3992WX | EPRAB3992WX |  | SO on sewer network | NZ0894652307 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | BACKSTONE BECK TRIB OF R.DERWE |  |  | Commissioned pre-2016 - full year data expected | 69.5 | 20 | 98.6%
Northumbrian Water | DAIRY LANE CSO SU024 | 6NW801425 | 245/A/0520 | 245/A/0520 |  | SO on sewer network | NZ3304749837 | GB103024077580 | Lumley Park Burn from Source to Herrington Burn | RAINTON BURN |  |  | Commissioned pre-2016 - full year data expected | 22.25 | 9 | 99.98%
Northumbrian Water | DALE STREET CSO (REF.L27) | 6NW801614 | Not on public register | 25/06/1030 |  | SO on sewer network | NZ6296422768 | GB650301500005 | Tees Coastal | Long Beck |  | Marske | Commissioned pre-2016 - full year data expected | 0.23333 | 4 | 100%
Northumbrian Water | DALTON-LE-DALE CSO | 6NW801520 | 255/D/0277 | 255/D/0277 |  | SO on sewer network | NZ4151148303 | GB103025075970 | Dalton Beck to North Sea | DAWDON DENE BECK |  | Seaham Hall | Commissioned pre-2016 - full year data expected | 646.4006 | 66 | 89.54% | Comms failure / issue | Resolved - December | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution
Northumbrian Water | DALTON PIERCY SPS | 6NW800640 | 254/1077 | 254/1077 | A1 | Storm discharge at pumping station | NZ4670131075 | GB103025076030 | Greatham Beck Catchment (trib of Tidal Tees) | DALTON BECK |  |  | Commissioned pre-2016 - full year data expected | 83.5 | 21 | 99.61%
Northumbrian Water | DALTON RETAIL PARK CSO | 6NW800404 | EPRBB3793WU | EPRBB3793WU |  | SO on sewer network | NZ4026446581 | GB103025075970 | Dalton Beck to North Sea | DALTON BURN |  |  | September 2021 | 96.25 | 11 | 13.62% | Sensor failure / issue | N/A - Ongoing investigation
Northumbrian Water | DAPHNE CRESCENT CSO | 6NW801534 | NPSWQD005830 | NPSWQD005830 |  | SO on sewer network | NZ4206548416 | GB103025075970 | Dalton Beck to North Sea | TRIB OF DAWDON DENE |  |  | Commissioned pre-2016 - full year data expected | 0.75 | 3 | 99.99%
Northumbrian Water | DARLINGTON BRUNSWICK STREET CSO | 6NW800343 | EPRCB3094AD | EPRCB3094AD |  | SO on sewer network | NZ2915514594 | GB103025072596 | Skerne from Demons Beck to Tees | RIVER SKERNE |  |  | Commissioned in 2017 - full year data expected | 139 | 34 | 97.75%
Northumbrian Water | DARLINGTON CROWN STREET NO 34 CSO | 6NW801327 | EPRCB3095WD | EPRCB3095WD |  | SO on sewer network | NZ2914214533 | GB103025072596 | Skerne from Demons Beck to Tees | RIVER SKERNE |  |  | Commissioned pre-2016 - full year data expected | 23 | 14 | 99.99%
Northumbrian Water | DENE GROVE CSO Brinkburn Dene | 6NW000003 | 253/1921 | 253/1921 |  | SO on sewer network | NZ2766015342 | GB103025072596 | Skerne from Demons Beck to Tees | COCKER BECK |  |  | Commissioned pre-2016 - full year data expected | 2 | 4 | 99.99%
Northumbrian Water | DARLINGTON LANE SSO | 6NW801545 | 25/04/1623 | 25/04/1623 |  | SO on sewer network | NZ4370021100 | GB103025072550 | Lustrum Beck Catchment (trib of Tees) | LUSTRUM BECK |  |  | Commissioned pre-2016 - full year data expected | 4.5 | 14 | 99.99%
Northumbrian Water | DAVY BANK PUMPING STATION | 6NW801374 | 235/1687 | 235/1687 | A1 | Storm discharge at pumping station | NZ3088066010 | GB510302310200 | TYNE | TYNE SALINE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 23.5 | 26 | 99.73%
Northumbrian Water | DEAN ROAD CSO | 6NW801336 | EPRBB3495RJ | EPRBB3495RJ |  | SO on sewer network | NZ2942431801 | GB103025072520 | Carrs from Source to Skerne | TRIBUTARY OF RIVER SKERNE |  |  | Commissioned pre-2016 - full year data expected | 4.25 | 9 | 99.38%
Northumbrian Water | DEAN STREET CSO | 6NW800315 | 235/1921 | 235/1921 |  | SO on sewer network | NZ2526063810 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | Commissioned in 2020 - full year data expected | 0.0175 | 1 | 97.98%
Northumbrian Water | DEEPDALE AVENUE NO2 CSO (M007) | 6NW801574 | 254/1815 | 254/1815 |  | SO on sewer network | NZ5006017810 | GB103025072210 | Marton West Beck Catchment (trib of Tidal Tees) | MARTON WEST BECK |  |  | Commissioned pre-2016 - full year data expected | 1.25 | 2 | 99.99%
Northumbrian Water | DELLWOOD PUMPED STORAGE TANK CSO | 6NW801135 | 242/1042 | 242/1042 |  | SO on sewer network | NZ2142429782 | GB103024072730 | Gaunless from Hummer Beck to Wear | RIVER GAUNLESS |  |  | Commissioned pre-2016 - full year data expected | 2085.5 | 147 | 99.88% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
Northumbrian Water | BARNARD CASTLE STW CSO INLET Demesne Mill CSO (East) | 6NW800928 | 252/A/0559 | 252/A/0559 |  | SO on sewer network | NZ0523215935 | GB103025072512 | Tees from Percy Beck to River Greta | RIVER TEES |  |  | Commissioned pre-2016 - full year data expected | 16.25 | 12 | 86.56% | Comms failure / issue | Scheduled
Northumbrian Water | DEMESNES MILL CSO | 6NW800927 | 252/1124 | 252/1124 |  | SO on sewer network | NZ0529815894 | GB103025072512 | Tees from Percy Beck to River Greta | RIVER TEES |  |  | Commissioned pre-2016 - full year data expected | 6.75 | 9 | 99.65%
Northumbrian Water | DEMESNES MILL NO 3 CSO | 6NW800926 | 252/1066 | QC.25/02/1066 |  | SO on sewer network | NZ0529815894 | GB103025072512 | Tees from Percy Beck to River Greta | River Tees |  |  | Commissioned pre-2016 - full year data expected | 5.75 | 3 | 93.04%
Northumbrian Water | DENE AVENUE CSO NC051 | 6NW801070 | 233/1271 | 233/1271 |  | SO on sewer network | NZ1893665111 | 8 | #N/A | SUGLEY DENE (RIVER TYNE) |  |  | Commissioned pre-2016 - full year data expected | 15.25 | 13 | 99.99%
Northumbrian Water | DENE HALL DRIVE CSO | 6NW801100 | EPRCB3290DR | EPRCB3290DR |  | SO on sewer network | NZ1973729001 | GB103024077463 | Wear from Beechburn Beck to Gaunless | COAL BURN |  |  | Commissioned pre-2016 - full year data expected | 20.5 | 13 | 99.99%
Northumbrian Water | DENE HOUSE SPS | 6NW800555 | 224/1004 | 224/1004 | A1 | Storm discharge at pumping station | NZ2888091280 | 362 | #N/A | RIVER LYNE |  |  | Commissioned in 2020 - full year data expected | 443.265 | 47 | 100%
Northumbrian Water | DENECREST CSO | 6NW800966 | 234/0999 | 234/0999 |  | SO on sewer network | NZ1121054710 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | EBCHESTER BURN |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | DENE HOLME OUTFALL TIDAL TANK | 6NW800793 | 255/1148 | 255/1148 | 255/1148-01 | Storm discharge at pumping station | NZ4583040760 | GB103025075930 | Castle Eden Burn from Source to North Sea | NORTH SEA |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | DENE HOLME SEWAGE PUMPING STATION TIDAL TANK | 6NW800792 | 255/1149 | 255/1149 | 255/1149-01 | Storm discharge at pumping station | NZ4519040420 | GB103025075930 | Castle Eden Burn from Source to North Sea | CASTLE EDEN BURN |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | DENESIDE CSO | 6NW801160 | 244/0959 | 244/0959 |  | SO on sewer network | NZ2361045880 | GB103024077551 | Browney from Smallhope Burn Deerness confl | DENE BURN |  |  | Commissioned pre-2016 - full year data expected | 18.25 | 20 | 98.4%
Northumbrian Water | BEVAN HOUSE DENT STREET | 6NW801400 | 226/1059 | 226/1059 |  | SO on sewer network | NZ3207980783 | GB510302203200 | BLYTH (N) | BLYTH ESTUARY |  | Blyth South Beach | Commissioned pre-2016 - full year data expected | 44.4 | 7 | 100%
Northumbrian Water | DENTON DENE NORTH OF WEST ROAD CSO | 6NW801123 | 235/1869 | 235/1869 |  | SO on sewer network | NZ1965463974 | GB510302310200 | TYNE | RIVER TYNE (SALINE ESTUARY) |  |  | Commissioned pre-2016 - full year data expected | 7.7667 | 13 | 95.52%
Northumbrian Water | DENTON ROAD CSO NC027 | 6NW800266 | 235/1937 | 235/1937 |  | SO on sewer network | NZ1965463974 | GB510302310200 | TYNE | RIVER TYNE |  |  | Commissioned in 2018 - full year data expected | 592.6997 | 101 | 100%
Northumbrian Water | DEPTFORD PUMPING STATION | 6NW800607 | 245/1212 | 245/1212 | 245/1212-01 | Storm discharge at pumping station | NZ3839057810 | GB510302402900 | WEAR | RIVER WEAR (SALINE ESTUARY) |  |  | Commissioned pre-2016 - full year data expected | 309 | 61 | 98.4% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | DERWENT CARAVAN PARK PUMPING STN | 6NW801030 | 234/1129 | 234/1129 |  | SO on sewer network | NZ1690058500 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | DERWENT |  |  | Commissioned pre-2016 - full year data expected | 2.25 | 1 | 90.03%
Northumbrian Water | DERWENT WATER TERRACE CSO BT022 | 6NW800841 | EPRAB3090VG | EPRAB3090VG |  | SO on sewer network | NU0236149575 | GB650301440000 | Northumberland North | NORTH SEA |  | Spittal | Commissioned pre-2016 - full year data expected | 61.4411 | 13 | 99.86%
Northumbrian Water | DERWENTSIDE HOUSE CSO | 6NW800967 | 234/1142 | 234/1142 |  | SO on sewer network | NZ1155056760 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | DERWENT |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | DEVONSHIRE ROAD EAST CSO | 6NW801361 | EPRCP3526GZ | EPRCP3526GZ |  | SO on sewer network | NZ3106842585 | GB103024077540 | Pittington Beck from Coalford to Old Durham Beck | TRIBUTARY OF PITTINGTON BECK |  |  | Commissioned pre-2016 - full year data expected | 0.5 | 2 | 99.99%
Northumbrian Water | DEVONSHIRE ROAD WEST CSO | 6NW801360 | EPRCP3525XM | EPRCP3525XM |  | SO on sewer network | NZ3106842585 | GB103024077540 | Pittington Beck from Coalford to Old Durham Beck | TRIBUTARY OF PITTINGTON BECK |  |  | Commissioned pre-2016 - full year data expected | 1 | 2 | 99.99%
Northumbrian Water | DINNINGTON EAST SPS | 6NW800523 | 226/0102 | 226/0102 | 226/0102-01 | Storm discharge at pumping station | NZ2140073270 | GB103022076190 | Seaton Burn from Source to Tidal Limit | HARTLEY BURN |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | DINNINGTON WEST SPS | 6NW800520 | 226/0204 | 226/0204 | A1 | Storm discharge at pumping station | NZ2015073310 | GB103022076870 | Ponteland to Dinnington Catchment Area | PRESTWICK CARR |  |  | Commissioned in 2016 - full year data expected | 202.75 | 32 | 99.74%
Northumbrian Water | DIPTON STW CSO Inlet | 6NW800155 | 234/D/0005 | 234/D/0005 |  | Inlet SO at WwTW | NZ1580154448 | GB103023074780 | Pont Burn Catchment (trib of Derwent) | Dipton Burn |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | DIPTON STW STORM TANK | 6NW800732 | 234/A/0657 | 234/A/0657 |  | Storm tank at WwTW | NZ1582054374 | GB103023074780 | Pont Burn Catchment (trib of Derwent) | Dipton Burn |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | DIPWOOD ROAD CSO GO16 | 6NW801008 | 234/1126 | 234/1126 |  | SO on sewer network | NZ1595858053 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | DERWENT, TRIBUTARY OF |  |  | Commissioned pre-2016 - full year data expected | 45.5 | 31 | 91.47%
Northumbrian Water | DOCK ROAD CSO (BT44) | 6NW800209 | 210/1363 | 210/1363 |  | SO on sewer network | NT9987152110 | GB510202110000 | TWEED | RIVER TWEED |  | Spittal | Commissioned pre-2016 - full year data expected | 107.0667 | 49 | 100% |  |  | Performance - Infiltration | N/A - Ongoing investigation
Northumbrian Water | DON VALLEY PUMPING STATION | 6NW800685 | 235/B/0171 | Permit Anomaly - EO permit 235/B/0171 | To be permitted for storm | Storm discharge at pumping station | NZ3355864930 | 8 | #N/A | River Don |  |  | Commissioned in 2020 - full year data expected | 142.9556 | 28 | 99.8%
Northumbrian Water | COACH ROAD EST CSO DONWELL PRIMARY SCHOOL | 6NW801369 | 235/1951 | 235/1951 |  | SO on sewer network | NZ3115058340 | GB103023075690 | Don from Source to Tidal Limit | USWORTH BURN |  |  | Commissioned pre-2016 - full year data expected | 183 | 36 | 99.93%
Northumbrian Water | DORMER WAY PS | 6NW801591 | 254/1808 | 254/1808 |  | SO on sewer network | NZ5242120275 | 10 | #N/A | NORMANBY BECK |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | DOWNE STREET SPS CSO | 6NW800673 | 256/1077 | 256/1077 | 256/1077-01 | Storm discharge at pumping station | NZ7127318283 | GB103025071940 | Middle Gill Beck from Source to Kilton Beck | WHITECLIFF BECK |  |  | Commissioned pre-2016 - full year data expected | 263.5 | 36 | 95.47%
Northumbrian Water | DRYSDALE CRESENT CSO | 6NW801171 | 226/1252 | 226/1252 |  | SO on sewer network | NZ2359172978 | GB103022076190 | Seaton Burn from Source to Tidal Limit | HARTLEY BURN |  |  | Commissioned pre-2016 - full year data expected | 10.75 | 7 | 99.97%
Northumbrian Water | DUDLEY FIRST SCHOOL CSO | 6NW801252 | 226/1257 | 226/1257 |  | SO on sewer network | NZ2612873487 | GB103022076190 | Seaton Burn from Source to Tidal Limit | SEATON BURN |  |  | Commissioned pre-2016 - full year data expected | 0.5 | 2 | 99.87%
Northumbrian Water | DUDLEY MIDDLE SCHOOL CSO | 6NW801254 | 226/1259 | 226/1259 |  | SO on sewer network | NZ2658373756 | GB103022076190 | Seaton Burn from Source to Tidal Limit | SANDY'S LETCH,TRIB SEATON BURN |  |  | Commissioned pre-2016 - full year data expected | 18.75 | 10 | 99.99%
Northumbrian Water | DUKE STREET CSO | 6NW801027 | 235/1714 | 235/1714 |  | SO on sewer network | NZ1687452291 | GB103023075670 | Team from Source to Tyne | TRIB KYO BURN |  |  | Commissioned pre-2016 - full year data expected | 15.25 | 21 | 99.72%
Northumbrian Water | DUKES WALK CSO (NTY031) (A63) | 6NW800387 | 235/1982 | 235/1982 |  | SO on sewer network | NZ3518373399 | GB650301500002 | Tyne and Wear | NORTH SEA |  | Whitley Bay | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
Northumbrian Water | DUNN STREET | 6NW801636 | 235/1929 | 235/1929 |  | SO on sewer network | NZ1687052290 | GB103023075670 | Team from Source to Tyne | KYO BURN |  |  | Commissioned pre-2016 - full year data expected | 24 | 13 | 99.98%
Northumbrian Water | DUNSTAN SEWAGE TREATMENT WORKS | 6NW800121 | 221/0912 | 221/0912 | 221/0912-02 | Inlet SO at WwTW | NU2590020080 | GB650301500001 | Northumberland South | CRASTER BURN |  |  | Commissioned in 2020 - full year data expected | 62.0028 | 6 | 99.29%
Northumbrian Water | DUNSTON FLOUR MILL (WEST) CSO | 6NW801150 | 235/1738 | 235/1738 |  | SO on sewer network | NZ2257962750 | GB510302310200 | TYNE | RIVER TYNE SALINE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 459.8333 | 35 | 98.58%
Northumbrian Water | PELAW WOOD SEWER, NO 1 BATHS BRIDGE | 6NW450106 | 245/0914 | 245/0914 |  | SO on sewer network | NZ2775642518 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | WEAR |  |  | Commissioned pre-2016 - full year data expected | 62 | 34 | 98.17%
Northumbrian Water | DURHAM ROAD REF NO 36 | 6NW801633 | 234/1152 | 234/1152 |  | SO on sewer network | NZ1002151801 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | TINKERHILL GILL, TRIBUTARY OF |  |  | Commissioned pre-2016 - full year data expected | 4 | 9 | 99.97%
Northumbrian Water | DURHAM ROAD CSO | 6NW801284 | 235/1884 | 235/1884 |  | SO on sewer network | NZ2657055590 | GB103023075670 | Team from Source to Tyne | ROWLETCH BURN |  |  | Commissioned pre-2016 - full year data expected | 1.75 | 3 | 99.99%
Northumbrian Water | DURHAM ROAD CSO | 6NW801303 | 243/E/0569 | 243/E/0569 |  | SO on sewer network | NZ2839533383 | GB103023075670 | Team from Source to Tyne | UNNAMED TRIB OF TURSDALE BECK |  |  | Commissioned pre-2016 - full year data expected | 6.25 | 15 | 91.9%
Northumbrian Water | DURHAM ROAD CSO | 6NW801113 | 245/1076 | 245/1076 |  | SO on sewer network | NZ2075951817 | GB103023075670 | Team from Source to Tyne | STANLEY BURN TRIBUTARY |  |  | Commissioned pre-2016 - full year data expected | 0.75 | 1 | 99.94%
Northumbrian Water | DURHAM SKILL CENTRE CSO DU008 | 6NW801197 | 244/1017 | 244/1017 |  | SO on sewer network | NZ2540239889 | GB103024077552 | Browney from Deerness confl to Wear | GOAT'S BECK TRIB RIVER BROWNEY |  |  | Commissioned pre-2016 - full year data expected | 13.5 | 14 | 97.14%
Northumbrian Water | DURHAM STREET CSO | 6NW801521 | 255/1155 | 255/1155 |  | SO on sewer network | NZ4153049819 | 367 | #N/A | ICE HOUSE DEAN |  | Seaham Hall | Commissioned pre-2016 - full year data expected | 0.56639 | 5 | 95.58%
Northumbrian Water | DURHAM UNIVERSITY STW CSO INLET | 6NW800167 | 245/1064 | 245/1064 | C | Inlet SO at WwTW | NZ2736039830 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | SALTWELL GILL |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | DURHAM UNIVERSITY STW Storm Tank | 6NW800766 | 245/1064 | 245/1064 | B | Storm tank at WwTW | NZ2736039830 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | SALTWELL GILL |  |  | Commissioned in 2020 - full year data expected | 557.5447 | 57 | 74.68% | Capital / maintenance works affect EDM operation | N/A - Ongoing investigation
Northumbrian Water | EASSON ROAD/DODDS STREET CSO | 6NW801001 | EPRBB3695WG | EPRBB3695WG |  | SO on sewer network | NZ2918014935 | GB103025072596 | Skerne from Demons Beck to Tees | RIVER SKERNE |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 92.48%
Northumbrian Water | EAST BOLDON CSO NO 6 | 6NW801491 | 235/F/0616 | 235/F/0616 |  | SO on sewer network | NZ3732361344 | GB103023075690 | Don from Source to Tidal Limit | DON |  |  | Commissioned pre-2016 - full year data expected | 52.5 | 26 | 45.35% | Comms failure / issue | Scheduled | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | EAST END CSO | 6NW800935 | 241/1092 | 241/1092 |  | SO on sewer network | NZ0780037210 | GB103024077520 | Waskerley Beck from Source to Wear | WASKERLEY BECK |  |  | Commissioned pre-2016 - full year data expected | 60.5 | 35 | 99.99%
Northumbrian Water | EAST END CSO (SE 026) | 6NW800379 | 253/1264 | 253/1264 |  | SO on sewer network | NZ3616929104 | GB103024077520 | Waskerley Beck from Source to Wear | TRIBUTARY OF REDCAR BECK |  |  | Commissioned in 2017 - full year data expected | 55 | 37 | 80.01% | Comms failure / issue | Resolved - November
Northumbrian Water | EAST FARM CSO | 6NW801009 | 233/1081 | 233/1081 |  | SO on sewer network | NZ1558061680 | GB103023074791 | Blaydon Burn | BARLOW BURN |  |  | Commissioned pre-2016 - full year data expected | 8 | 9 | 99.91%
Northumbrian Water | EAST FORD ROAD PS | 6NW800550 | 225/0939 | 225/0939 | A | Storm discharge at pumping station | NZ2713085930 | GB103022077062 | Wansbeck from Bothal Burn to North Sea | WANSBECK ESTUARY |  |  | Commissioned in 2020 - full year data expected | 8.8972 | 20 | 99.6%
Northumbrian Water | EAST HARTFORD PS | 6NW800548 | 226/1089 | 226/1089 | 226/1089-02 | Storm discharge at pumping station | NZ2720079350 | GB103022077052 | Blyth from Pont to Tidal Limit | HORTON BURN (RIVER BLYTH) |  |  | Commissioned pre-2016 - full year data expected | 481.75 | 45 | 96.33%
Northumbrian Water | EAST HENDON ROAD CSO | 6NW801512 | EPRCB3199EC | EPRCB3199EC |  | SO on sewer network | NZ4108456147 | GB650301500002 | Tyne and Wear | NORTH SEA |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | EAST HOWLE STW | 6NW800169 | 243/1026 | 243/1026 | A2 | Inlet SO at WwTW | NZ2956633917 | GB103024077410 | Croxdale Beck from Source to Wear | AN UNNAMED TRI RIVER WEAR |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | EAST OF KNITSLEY GRANGE FARM CSO | 6NW800976 | 244/0997 | 244/0997 |  | SO on sewer network | NZ1223548250 | GB103024077330 | Smallhope Burn from Source to Browney, Stocke | SMALLHOPE BURN |  |  | Commissioned pre-2016 - full year data expected | 67.5 | 30 | 67.5% | Comms failure / issue | Resolved - April
Northumbrian Water | SLEEKBURN EAST CSO | 6NW801321 | 226/1272 | 226/1272 | 226/1272-01 | Storm discharge at pumping station | NZ2864083400 | GB510302203200 | BLYTH (N) | SLEEK BURN |  |  | Commissioned pre-2016 - full year data expected | 84.5 | 27 | 97.27%
Northumbrian Water | EAST STREET WAS SWINBURN ST END CSO | 6NW800318 | 235/1924 | 235/1924 |  | SO on sewer network | NZ2526963670 | GB510302310200 | TYNE | RIVER TYNE |  |  | Commissioned in 2018 - full year data expected | 10.2311 | 16 | 99.98%
Northumbrian Water | EAST TANFIELD STW CSO INLET | 6NW801090 | 235/1871 | 235/1871 | A3 | Inlet SO at WwTW | NZ1973655324 | GB103023075670 | Team from Source to Tyne | CAUSEY BURN |  |  | Commissioned in 2018 - full year data expected | 767.1086 | 106 | 100%
Northumbrian Water | EAST TANFIELD STW Storm Tank | 6NW800740 | 235/1871 | 235/1871 | A2 | Storm tank at WwTW | NZ1973655324 | GB103023075670 | Team from Source to Tyne | CAUSEY BURN |  |  | Commissioned in 2019 - full year data expected | 2217.8981 | 129 | 99.9%
Northumbrian Water | EAST TERRACE CSO | 6NW801551 | 255/1190 | 255/1190 |  | SO on sewer network | NZ4435037890 | GB103025075910 | Crimdon Beck from Source to Sea | TRIB. OF HEADS HOPE BURN |  |  | Commissioned pre-2016 - full year data expected | 10.9333 | 11 | 99.57%
Northumbrian Water | EAST VIEW CSO | 6NW801085 | 245/1074 | 245/1074 |  | SO on sewer network | NZ1907051470 | GB103024077590 | Twizell Burn from Source to Cong Burn | STANLEY BURN |  |  | Commissioned pre-2016 - full year data expected | 2.75 | 4 | 99.98%
Northumbrian Water | EASTBOURNE EAST & WEST CSO | 6NW800420 | 254/1843 | 254/1843 |  | SO on sewer network | NZ4431920120 | GB103025072550 | Lustrum Beck Catchment (trib of Tees) | LUSTRUM BECK |  |  | Commissioned in 2019 - full year data expected | 115.4125 | 44 | 99.95%
Northumbrian Water | EASTBOURNE SOUTH CSO | 6NW801549 | 254/1380 | 254/1380 |  | SO on sewer network | NZ4432020119 | GB103025072550 | Lustrum Beck Catchment (trib of Tees) | LUSTRUM BECK |  |  | Commissioned pre-2016 - full year data expected | 245 | 54 | 99.98%
Northumbrian Water | EASTERN AVENUE CSO | 6NW800269 | 235/F/0651 | 235/F/0651 |  | SO on sewer network | NZ2464059880 | GB103023075670 | Team from Source to Tyne | TEAM |  |  | Commissioned pre-2016 - full year data expected | 135.25 | 40 | 99.44%
Northumbrian Water | EASTERN WAY SSO | 6NW801034 | 226/A/0971 | 226/A/0971 |  | SO on sewer network | NZ1581072500 | GB103022076860 | Pont from Med Burn to Small Burn | PONT |  |  | Commissioned pre-2016 - full year data expected | 302.25 | 41 | 99.67%
Northumbrian Water | EBCHESTER SPS | 6NW800502 | 234/0989 | 234/0989 | A1 | Storm discharge at pumping station | NZ1003055550 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | DERWENT |  |  | Commissioned in 2020 - full year data expected | 550.4436 | 67 | 99.95%
Northumbrian Water | EDEN WALK CSO | 6NW801433 | 235/1969 | 235/1969 |  | SO on sewer network | NZ3343663192 | GB103023075690 | Don from Source to Tidal Limit | RIVER DON |  |  | Commissioned pre-2016 - full year data expected | 45.75 | 32 | 96.69%
Northumbrian Water | EDINBURGH DRIVE CSO | 6NW801223 | 253/1076 | 253/1076 |  | SO on sewer network | NZ2634713714 | GB103025072190 | Tees from River Greta to River Skerne | TEES TRIBUTARY |  |  | Commissioned pre-2016 - full year data expected | 4.25 | 5 | 66.73% | Comms failure / issue | Scheduled
Northumbrian Water | EDMONDSLEY STW | 6NW800754 | 245/0839 | 245/0839 |  | Storm tank at WwTW | NZ2375950175 | GB103024077560 | Cong Burn from Source to Twizell Burn | HUMBLE BURN |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | EDNA STREET CSO | 6NW801671 | 243/0981 | 243/0981 |  | SO on sewer network | NZ3059037810 | GB103024077410 | Croxdale Beck from Source to Wear | BOWBURN BECK |  |  | Commissioned pre-2016 - full year data expected | 168.25 | 43 | 99.99%
Northumbrian Water | EGGLESCLIFFE BANK CSO | 6NW801525 | 254/1179 | 254/1179 |  | SO on sewer network | NZ4191713137 | GB103025072595 | Tees from Skerne to Tidal Limit | TEES ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 105.0667 | 72 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | EGGLESTON STW SSO | 6NW800909 | 251/0926 | 251/0926 |  | SO on sewer network | NY9940023400 | GB103025072511 | Tees from Maize Beck to Percy Beck | TEES |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | EGLINGHAM STW | 6NW800114 | 222/0043 | Permit Anomaly - STW permit 222/0043 | To be permitted for storm | Inlet SO at WwTW | NU1140718901 | GB103022076390 | Eglingham Burn from Source to Shipley Burn | Eglingham Burn |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | EILANS GATE CSO | 6NW800895 | 233/1241 | 233/1241 |  | SO on sewer network | NY9310064400 | GB103023075801 | Tyne from Watersmeet to Tidal Limit | COCKSHAW BURN |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 90.21%
Northumbrian Water | ELAND LANE (NEW) PUMPING STATION | 6NW801036 | 226/A/0965 | 226/A/0965 | 226/A/0965 Condition 1 (Storm Sewage) | Storm discharge at pumping station | NZ1663072980 | GB103022076860 | Pont from Med Burn to Small Burn | PONT |  |  | Commissioned pre-2016 - full year data expected | 2 | 3 | 97.32%
Northumbrian Water | ELAND LANE (NEW) PUMPING STATION | 6NW800679 | 226/G/0174 | 226/G/0174 |  | Storm discharge at pumping station | NZ1662472984 | GB103022076860 | Pont from Med Burn to Small Burn | River Pont |  |  | Commissioned in 2020 - full year data expected | 1196.9 | 90 | 99.99%
Northumbrian Water | ELDER COTTAGES CSO | 6NW801097 | 225/1076 | 225/1076 |  | SO on sewer network | NZ1978285203 | GB103022077061 | Wansbeck from Font to Bothal Burn | CHURCH BURN |  |  | Commissioned pre-2016 - full year data expected | 56.75 | 21 | 93.99%
Northumbrian Water | ELDON STREET CSO | 6NW801472 | 235/1944 | 235/1944 |  | SO on sewer network | NZ3534566008 | GB510302310200 | TYNE | RIVER TYNE ESTUARINE WATERS |  |  | Commissioned pre-2016 - full year data expected | 411.75 | 68 | 99.79% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | ELEMORE VALE SPS | 6NW800595 | 245/1399 | 245/1399 | A1 | Storm discharge at pumping station | NZ3584045710 | GB103024077580 | Lumley Park Burn from Source to Herrington Burn | HETTON BURN, TRIBUTARY OF |  |  | Commissioned in 2020 - full year data expected | 0.3275 | 3 | 100%
Northumbrian Water | ELLINGHAM STW | 6NW800850 | 221/1056 | 221/1056 | 221/1056-03 | Inlet SO at WwTW | NU1717025740 | GB103022077070 | Long Nanny from Source to N Sea | ELLINGHAM BURN |  |  | Commissioned pre-2016 - full year data expected | 14.25 | 3 | 97%
Northumbrian Water | ELMWOOD GARDENS | 6NW801164 | 235/1568 | 235/1568 |  | SO on sewer network | NZ2409959833 | GB103023075670 | Team from Source to Tyne | BLACK BURN |  |  | Commissioned pre-2016 - full year data expected | 136.8333 | 63 | 100%
Northumbrian Water | ELSDON SEWAGE TREATMENT WORKS | 6NW800137 | 231/1027 | 231/1027 | A2 | Inlet SO at WwTW | NY9372992983 | GB103023075240 | Elsdon Burn Upper Catchment West | ELSDON BURN |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | ELVET SYPHON CSO | 6NW801270 | NPSWQD004521 | NPSWQD004521 |  | SO on sewer network | NZ2757842431 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | RIVER WEAR |  |  | Commissioned pre-2016 - full year data expected | 287.9667 | 57 | 56.64% | Comms failure / issue | Resolved - August
Northumbrian Water | ELWICK SPS | 6NW800634(1) | 254/1076 | 254/1076 | A1 | Storm discharge at pumping station | NZ4568432124 | GB103025076030 | Greatham Beck Catchment (trib of Tidal Tees) | CHAR BECK |  |  | Commissioned pre-2016 - full year data expected | 7.25 | 11 | 99.69%
Northumbrian Water | ELWIN PLACE CSO | 6NW801204 | 245/1275 | 245/1275 |  | SO on sewer network | NZ2549052510 | GB103024077600 | Cong Burn from Twizell Burn to Wear | TRIB OF CONG BURN |  |  | Commissioned pre-2016 - full year data expected | 20.75 | 20 | 99.48%
Northumbrian Water | SEA LANE PUMPING STATION EMBLETON LOW MILL | 6NW800472 | 221/0987 | 221/0987 | 221/0987-01 | Storm discharge at pumping station | NU2410022990 | GB103022076370 | Embleton Burn form Source to N Sea | EMBLETON BURN |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | EMBLETON SEWAGE WORKS CSO | 6NW800119 | 221/G/0336 | 221/G/0336 |  | Inlet SO at WwTW | NU2332021860 | GB103022076370 | Embleton Burn form Source to N Sea | EMBLETON BURN |  |  | Commissioned in 2020 - full year data expected | 262.6769 | 60 | 85.8% | Comms failure / issue | Resolved - August
Northumbrian Water | EPPLEBY COMBINED SEWER OVERFLOW | 6NW801038 | 252/1129 | 252/1129 |  | SO on sewer network | NZ1810013100 | GB103025072150 | Aldbrough Beck from Source to Clow Beck | FORCETT BECK |  |  | Commissioned pre-2016 - full year data expected | 52 | 17 | 99.45%
Northumbrian Water | EPPLEBY SEWAGE DISPOSAL WORKS | 6NW800739 | 25/02/1107 | 25/02/1107 | 25/02/1107-02 | Storm tank at WwTW | NZ1816013070 | GB103025072150 | Aldbrough Beck from Source to Clow Beck | FORCETT BECK (TEES CATCHMENT) |  |  | Commissioned in 2020 - full year data expected | 2174.1733 | 149 | 100% |  |  | Performance - Infiltration
Northumbrian Water | ESCOMB SPS | 6NW801074 | 241/1023 | 241/1023 | A1 | Storm discharge at pumping station | NZ1914130349 | GB103024077463 | Wear from Beechburn Beck to Gaunless | RIVER WEAR |  |  | Commissioned pre-2016 - full year data expected | 1000.5 | 56 | 99.92% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | ESH WINNING CSO POINT A2 | 6NW801045 | 244/E/0307 | 244/E/0307 |  | SO on sewer network | NZ1754140406 | GB103024077270 | Deerness from Source to Hedleyhope Burn | DEERNESS |  |  | Commissioned pre-2016 - full year data expected | 156 | 25 | 61.14% | Comms failure / issue | Resolved - November
Northumbrian Water | ESH WINNING SPS | 6NW800515 | 244/0884 | 244/0884 | A1 | Storm discharge at pumping station | NZ1921041540 | GB103024077270 | Deerness from Source to Hedleyhope Burn | DEERNESS |  |  | Commissioned in 2020 - full year data expected | 210.6831 | 42 | 100%
Northumbrian Water | ESH WINNING SEWAGE TREATMENT WORKS | 6NW800747 | 244/1026 | 244/1026 | A2 | Storm tank at WwTW | NZ2015742222 | GB103024077290 | Hedleyhope Burn from Source to Deerness | DEERNESS |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | MCCLEAN AVENUE CSO (REF NO L15) Eskdale Road | 6NW801602 | 254/1916 | 254/1916 |  | SO on sewer network | NZ5884123776 | GB103025072320 | Tees Estuary (S Bank) | Culverted Watercourse of Fleet Beck |  |  | Commissioned pre-2016 - full year data expected | 16.25 | 8 | 99.89%
Northumbrian Water | ESSEX CLOSE CSO | 6NW801168 | 235/1319 | 235/1319 |  | SO on sewer network | NZ2382462901 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 18.0667 | 25 | 100%
Northumbrian Water | ETAL STW | 6NW800104 | 210/0899 | 210/0899 | A2 | Inlet SO at WwTW | NT9264039550 | GB102021073050 | Till from Glen to River Tweed | TILL |  |  | Commissioned in 2020 - full year data expected | 90.3411 | 38 | 85.07% | Comms failure / issue | Resolved - Feburary
Northumbrian Water | ETHERLEY LANE (NO.100) CSO | 6NW801101 | EPRBB3997RC | EPRBB3997RC |  | SO on sewer network | NZ2028529160 | GB103024077463 | Wear from Beechburn Beck to Gaunless | CULVERTED TRIB RIVER WEAR |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 86.97% | Comms failure / issue | Resolved - July
Northumbrian Water | ETHERLEY LANE (NO.87) CSO | 6NW801102 | EPRBB3996AW | EPRBB3996AW |  | SO on sewer network | NZ2028529160 | GB103024077463 | Wear from Beechburn Beck to Gaunless | CULVERTED TRIB RIVER WEAR |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.98%
Northumbrian Water | ETHERLEY LANE CSO | 6NW801073 | 241/1156 | 241/1156 |  | SO on sewer network | NZ1943228844 | GB103024077463 | Wear from Beechburn Beck to Gaunless | COAL BURN |  |  | Commissioned pre-2016 - full year data expected | 490.25 | 75 | 99.6% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | EVENWOOD LANE CSO | 6NW801003 | NPSWQD006151 | NPSWQD006151 |  | SO on sewer network | NZ1601924497 | GB103024072690 | Gaunless from Source to Hummer Beck | CROOK BECK |  |  | Commissioned pre-2016 - full year data expected | 28.75 | 23 | 95.98%
Northumbrian Water | FACTORY ROAD CSO | 6NW800260 | 233/0911 | 233/0911 |  | SO on sewer network | NZ1883063669 | GB510302310200 | TYNE | TYNE (TIDAL) |  |  | Commissioned in 2018 - full year data expected | 116.4333 | 17 | 99.87%
Northumbrian Water | FAIR VIEW STORM SEWAGE OVERFLOW | 6NW801081 | 244/1014 | 244/1014 |  | SO on sewer network | NZ1922042050 | GB103024077290 | Hedleyhope Burn from Source to Deerness | PRIEST BURN |  |  | Commissioned pre-2016 - full year data expected | 133.75 | 24 | 99.89%
Northumbrian Water | FAIRFIELD INDUSTRIAL PARK SPS | 6NW800563 | 235/1749 | 235/1749 | A1 | Storm discharge at pumping station | NZ2937062960 | GB510302310200 | TYNE | RIVER TYNE SALINE ESTUARY |  |  | Commissioned in 2020 - full year data expected | 0.75 | 1 | 99.99%
Northumbrian Water | SHILBOTTLE CSO FAIRFIELD VIEW | 6NW800859 | 223/G/0089 | 223/G/0089 |  | SO on sewer network | NU2064008830 | GB103022076720 | Tyelaw Burn Catchment (trib of Coquet) | TYELAW BURN |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 97.26%
Northumbrian Water | FALSTONE & STANNERSBURN SEWAGE TREA | 6NW800126 | 231/A/0490 | 231/A/0490 |  | Inlet SO at WwTW | NY7230087000 | GB103023075070 | N Tyne from Lewis Burn to Tarset Burn | NORTH TYNE |  |  | May 2021 | #N/A | #N/A | 0% | Sensor failure / issue | N/A - Ongoing investigation
Northumbrian Water | FALSTONE & STANNERSBURN STW | 6NW800127 | 231/A/0491 | 231/A/0491 |  | Inlet SO at WwTW | NY7238087040 | GB103023075070 | N Tyne from Lewis Burn to Tarset Burn | NORTH TYNE |  |  | EDM to be installed by December 2023 | #N/A | #N/A | #N/A
Northumbrian Water | FARNE AVENUE CSO | 6NW801170 | 235/2004 | 235/2004 |  | SO on sewer network | NZ2406869449 | GB103023075780 | Ouse Burn from Source to Tyne | OUSEBURN |  |  | Commissioned pre-2016 - full year data expected | 6.25 | 9 | 99.81%
Northumbrian Water | FATFIELD CSO 3 | 6NW801390 | #TBC | Permit Anomaly | To be permitted for storm | SO on sewer network | NZ3148354141 | 9 | #N/A | River Wear |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | FELTON RECREATION GROUND CSO | 6NW800857 | 223/1004 | 223/1004 |  | SO on sewer network | NU1906300590 | GB103022076693 | Coquet from Forest Burn to Tidal Limit | RIVER COQUET |  |  | Commissioned pre-2016 - full year data expected | 54.25 | 26 | 47.51% | Comms failure / issue | Resolved - December
Northumbrian Water | FELTON STW CSO INLET | 6NW800117 | 223/0993 | 223/0993 | 223/0993-03 | Inlet SO at WwTW | NU1913000570 | GB103022076693 | Coquet from Forest Burn to Tidal Limit | COQUET |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | FELTON STW CSO Storm Tank | 6NW800694 | 223/0993 | 223/0993 | 223/0993-02 | Storm tank at WwTW | NU1913000570 | GB103022076693 | Coquet from Forest Burn to Tidal Limit | COQUET |  |  | Commissioned in 2020 - full year data expected | 2309.0956 | 137 | 99.92%
Northumbrian Water | FENWICK (BERWICK) STW | 6NW800112 | 221/0968 | 221/0968 | A2 | Inlet SO at WwTW | NU0683240072 | GB103022076490 | Fenham Burn Catchment (to N Sea) | Fenham Burn |  |  | Commissioned in 2020 - full year data expected | 454.9569 | 45 | 100%
Northumbrian Water | FERGUSON MOTOR REPAIRS CSO 2008 | 6NW800371 | EPRYB3435AJ | EPRYB3435AJ |  | SO on sewer network | NZ4332049097 | GB650301500002 | Tyne and Wear | SEAHAM SOUTH DOCK |  |  | Commissioned in 2020 - full year data expected | 0 | 0 | 70.25% | Comms failure / issue | Resolved - July
Northumbrian Water | ANNITSFORD BRIDGE CSO FERN DRIVE | 6NW800327 | 226/G/0058 | 226/G/0058 |  | SO on sewer network | NZ2691573580 | GB103022076190 | Seaton Burn from Source to Tidal Limit | Seaton Burn |  |  | Mar 2021 | #N/A | #N/A | 0% | Access - Unable to retrieve data from non-telemetry data logger (NB: not to be used for delayed access to fix existing fault) | Scheduled
Northumbrian Water | FERN DRIVE CSO | 6NW801256 | NPSWQD006838 | NPSWQD006838 |  | SO on sewer network | NZ2691273719 | GB103022076190 | Seaton Burn from Source to Tidal Limit | SEATON BURN |  |  | Commissioned pre-2016 - full year data expected | 33.25 | 11 | 99.99%
Northumbrian Water | FERNIE ROAD SSO | 6NW801610 | QR.25/06/0976 | QR.25/06/0976 |  | SO on sewer network | NZ6115015290 | GB103025071970 | Skelton Beck Catch (Saltburn) trib of North Sea | CHAPEL BECK |  |  | Commissioned pre-2016 - full year data expected | 28 | 7 | 99.98%
Northumbrian Water | FERRYBOAT LANE PUMPING STATION | 6NW801464 | 245/1208 | 245/1208 | 245/1208-01 | Storm discharge at pumping station | NZ3515057100 | GB510302402900 | WEAR | RIVER WEAR (SALINE ESTUARY) |  |  | Commissioned pre-2016 - full year data expected | 365 | 28 | 97.76%
Northumbrian Water | FERRYHILL NORTH SPS | 6NW801304 | 243/0978 | 243/0978 | A1 | Storm discharge at pumping station | NZ2844333428 | GB103024077410 | Croxdale Beck from Source to Wear | EAST HOWLE BECK |  |  | Commissioned pre-2016 - full year data expected | 56.5 | 44 | 99.97%
Northumbrian Water | FERRYHILL PS | 6NW800561 | 253/1037 | 253/1037 | A | Storm discharge at pumping station | NZ2960031650 | GB103025072520 | Carrs from Source to Skerne | MAINSFORTH STELL |  |  | Commissioned in 2020 - full year data expected | 35.0208 | 26 | 100%
Northumbrian Water | FIELDON BRIDGE CSO | 6NW801098 | 242/1041 | 242/1041 |  | SO on sewer network | NZ2048226845 | GB103024072730 | Gaunless from Hummer Beck to Wear | GAUNLESS |  |  | Commissioned pre-2016 - full year data expected | 143.25 | 15 | 85.1% | Sensor failure / issue | Resolved - March
Northumbrian Water | FIFTH ROW CSO | 6NW801262 | 224/0984 | 224/0984 |  | SO on sewer network | NZ2658091370 | GB103022076820 | Lyne from Source to Tidal Limit | POTLAND BURN |  |  | Commissioned pre-2016 - full year data expected | 2 | 5 | 41.58% | Sensor failure / issue | Resolved - November
Northumbrian Water | FINCHALE VIEW | 6NW801387 | 245/1294 | 245/1294 |  | SO on sewer network | NZ3003046450 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | WEAR |  |  | Commissioned pre-2016 - full year data expected | 150 | 69 | 99.42%
Northumbrian Water | LANGLEY PARK SEWAGE PS FINNINGS AVENUE | 6NW800518 | 244/A/0528 | 244/A/0528 | 244/A/0528-01 | Storm discharge at pumping station | NZ2039045080 | GB103024077551 | Browney from Smallhope Burn Deerness confl | BROWNEY |  |  | Commissioned in 2020 - full year data expected | 57.5078 | 25 | 99.98%
Northumbrian Water | FIR TREE STW | 6NW800727 | 241/1013 | 241/1013 | A2 | Storm tank at WwTW | NZ1369034173 | GB103024077462 | Wear from Houselop Beck to Beechburn Beck | WADLEY BURN |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | 29 FIRST ROW | 6NW800329 | 224/0969 | 224/0969 |  | SO on sewer network | NZ2646891153 | GB103022076820 | Lyne from Source to Tidal Limit | POTLAND BURN (TRIB OF R.LYNE) |  |  | Commissioned in 2017 - full year data expected | 4 | 7 | 99.99%
Northumbrian Water | FIRST SCHOOL CSO NTY002 | 6NW801172 | 226/G/0173 | 226/G/0173 |  | SO on sewer network | NZ2391373465 | GB103022076190 | Seaton Burn from Source to Tidal Limit | HARTLEY BURN |  |  | Commissioned pre-2016 - full year data expected | 343 | 55 | 99.94% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | FISH QUAY CSO | 6NW800392 | 235/1914 | 235/1914 | A | SO on sewer network | NZ3642068490 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | Commissioned in 2020 - full year data expected | 86.2311 | 21 | 100%
Northumbrian Water | FISHBURN BRIDGE CSO | 6NW801482 | NPSWQD008199 | NPSWQD008199 |  | SO on sewer network | NZ3615431350 | GB103025076070 | Skerne from Source to Carrs | RIVER SKERNE |  |  | Commissioned pre-2016 - full year data expected | 34 | 33 | 92.6%
Northumbrian Water | FISHBURN SEWAGE TREATMENT WORKS CSO INLET | 6NW800182 | 25/03/1234 | 25/03/1234 | 25/03/1234-03 | Inlet SO at WwTW | NZ3557031720 | GB103025076070 | Skerne from Source to Carrs | TRIB OF RIVER SKERNE |  |  | Commissioned in 2020 - full year data expected | 43.5147 | 15 | 100%
Northumbrian Water | FISHBURN SEWAGE TREATMENT WORKS CSO INLET | 6NW800786 | 25/03/1234 | 25/03/1234 | 25/03/1234-02 | Storm tank at WwTW | NZ3557031720 | GB103025076070 | Skerne from Source to Carrs | TRIB OF RIVER SKERNE |  |  | Commissioned in 2020 - full year data expected | 109.1747 | 28 | 74.97% | Comms failure / issue | Resolved - August
Northumbrian Water | FLOATERS MILL PS CSO | 6NW800362 | 245/E/0594 | 245/E/0594 | A1 | Storm discharge at pumping station | NZ3124850787 | GB103024077570 | Lumley Park Burn from Herrington Burn to R Wear | LUMLEY PARK BURN |  |  | Commissioned in 2020 - full year data expected | 0.063611 | 3 | 99.99%
Northumbrian Water | FORSTER STREET/EASSON ROAD CSO | 6NW800338 | EPRBB3791RD | EPRBB3791RD |  | SO on sewer network | NZ2918014935 | GB103025072596 | Skerne from Demons Beck to Tees | RIVER SKERNE |  |  | Commissioned pre-2016 - full year data expected | 0.25 | 1 | 99.99%
Northumbrian Water | FOUNDRY LANE NO 3 CSO | 6NW801244 | 235/1947 | 235/1947 |  | SO on sewer network | NZ2628764563 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 212.9667 | 44 | 62.84% | Comms failure / issue | Resolved - October
Northumbrian Water | FOUNDRY LANE NO1 CSO | 6NW801245 | 235/1528 | 235/1528 |  | SO on sewer network | NZ2624564671 | GB510302310200 | TYNE | OUSE BURN ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 199.7667 | 49 | 88.46% | Comms failure / issue | Resolved - May
Northumbrian Water | FOURSTONES STW STORM TANK | 6NW800704 | 232/1119 | 232/1119 | 232/1119-03 | Storm tank at WwTW | NY8859067610 | GB103023075710 | South Tyne from Allen to North Tyne | RIVER SOUTH TYNE |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | FRANKLAND LANE CSO | 6NW801273 | 245/1272 | 245/1272 |  | SO on sewer network | NZ2741543020 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | RIVER WEAR |  |  | Commissioned pre-2016 - full year data expected | 258.75 | 40 | 84% | Comms failure / issue | Scheduled | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | FRONT STREET (TOWN HALL) CSO | 6NW800812 | 232/1168 | 232/1168 |  | SO on sewer network | NY7172346568 | GB103023075531 | South Tyne from Black Burn to Tipalt Burn | RIVER NENT |  |  | Commissioned pre-2016 - full year data expected | 60 | 40 | 98.25%
Northumbrian Water | FRONT STREET CSO CH68 | 6NW801258 | 226/1180 | 226/1180 |  | SO on sewer network | NZ2653381522 | GB103022077052 | Blyth from Pont to Tidal Limit | RIVER BLYTH |  |  | Commissioned pre-2016 - full year data expected | 140.5 | 43 | 99.79%
Northumbrian Water | FRONT STREET CSO | 6NW801177 | 244/0927 | 244/0927 |  | SO on sewer network | NZ2500538681 | GB103024077552 | Browney from Deerness confl to Wear Water Body | BROWNEY TRIB |  |  | Commissioned pre-2016 - full year data expected | 29.4003 | 48 | 81.33% | Comms failure / issue | Resolved - March | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | FRONT STREET CSO | 6NW800277 | 244/0926 | 244/0926 |  | SO on sewer network | NZ2144445214 | GB103024077551 | Browney from Smallhope Burn Deerness confl Water Body | RIVER BROWNEY |  |  | Commissioned in 2017 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | FRONT STREET CSO | 6NW800278 | EPRJB3292WB | EPRJB3292WB |  | SO on sewer network | NZ2150845221 | GB103024077551 | Browney from Smallhope Burn Deerness confl Water Body | RIVER BROWNEY |  |  | Commissioned in 2017 - full year data expected | 284 | 62 | 82.86% | Comms failure / issue | Resolved - June | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | FRONT STREET CSO CH68 | 6NW801279 | 245/1315 | 245/1315 |  | SO on sewer network | NZ2743851607 | GB103024077600 | Cong Burn from Twizell Burn to Wear | CHESTER BURN |  |  | Commissioned pre-2016 - full year data expected | 0.75 | 2 | 97.13%
Northumbrian Water | FROSTERLEY SEWAGE TREATMENT WORKS | 6NW800145 | 241/1104 | 241/1104 | 241/1104-03 | Inlet SO at WwTW | NZ0456036930 | GB103024077461 | Wear from Middlehope Burn to Houselop Beck | WEAR |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | FURNESS PS OUTFALL | 6NW800650 | QR.25/04/1543 | QR.25/04/1543 | S1 | Storm discharge at pumping station | NZ4904022020 | GB510302509900 | TEES | THE RIVER TEES-SALINE ESTUARY |  |  | Commissioned in 2020 - full year data expected | 163.7058 | 17 | 100%
Northumbrian Water | GAINFORD SEWAGE TREATMENT WORKS CSO INLET | 6NW801039 | 25/02/1078 | 25/02/1078 | 25/02/1078-04 | Inlet SO at WwTW | NZ1771016320 | GB103025072190 | Tees from River Greta to River Skerne | RIVER TEES |  |  | Commissioned pre-2016 - full year data expected | 53.5 | 15 | 53.34% | Sensor failure / issue | Resolved - December
Northumbrian Water | GAINFORD SEWAGE TREATMENT WORKS CSO INLET | 6NW800735 | 25/02/1078 | 25/02/1078 | 25/02/1078-03 | Storm tank at WwTW | NZ1771016320 | GB103025072190 | Tees from River Greta to River Skerne | RIVER TEES |  |  | Commissioned in 2020 - full year data expected | 1196.7067 | 76 | 100%
Northumbrian Water | GALGATE CSO | 6NW800229 | 252/1122 | 252/1122 |  | SO on sewer network | NZ0479416561 | GB103025072512 | Tees from Percy Beck to River Greta | RIVER TEES |  |  | Commissioned in 2017 - full year data expected | 2.5 | 5 | 99.99%
Northumbrian Water | GARDNER AVENUE CSO | 6NW801638 | 243/1025 | 243/1025 |  | SO on sewer network | NZ1947034630 | GB103024077464 | Wear from Gaunless to Browney | WILLINGTON BURN |  |  | Commissioned pre-2016 - full year data expected | 2.5 | 7 | 97.37%
Northumbrian Water | GAS LANE CSO | 6NW800259 | 235/1740 | 235/1740 |  | SO on sewer network | NZ1842063569 | GB510302310200 | TYNE | RIVER TYNE SALINE ESTUARY |  |  | Commissioned in 2020 - full year data expected | 0 | 0 | 90.17%
Northumbrian Water | GELLESFIELD CSO | 6NW801118 | 234/1059 | 234/1059 |  | SO on sewer network | NZ2089659556 | GB103023075670 | Team from Source to Tyne | BLACK BURN |  |  | Commissioned pre-2016 - full year data expected | 296.25 | 64 | 99.59% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | GILL CEMETERY CSO (SU061) M2 | 6NW801503M2 | 245/1371 | 245/1371 | A1 | SO on sewer network | NZ3925257487 | GB510302402900 | WEAR | WEAR (SALINE ESTUARY) |  |  | Commissioned pre-2016 - full year data expected | 4.5 | 8 | 99.75% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | GILL CEMETERY CSO (SU061) M2 | 6NW801503M3 | 245/1371 | 245/1371 | A1 | SO on sewer network | NZ3925257487 | GB510302402900 | WEAR | WEAR (SALINE ESTUARY) |  |  | Commissioned in 2019 - full year data expected | 6.4289 | 11 | 100%
Northumbrian Water | GILLAS LANE EAST CSO (SU32) | 6NW801449 | 245/1360 | 245/1360 |  | SO on sewer network | NZ3478048810 | GB103024077580 | Lumley Park Burn from Source to Herrington Burn | ROUGH DENE BURN |  |  | Commissioned pre-2016 - full year data expected | 1 | 2 | 99.99%
Northumbrian Water | GILLAS LANE WEST CSO (SU30) | 6NW801424 | 245/1359 | 245/1359 |  | SO on sewer network | NZ3386048750 | GB103024077580 | Lumley Park Burn from Source to Herrington Burn | RAINTON BURN |  |  | Commissioned pre-2016 - full year data expected | 79.25 | 40 | 99.99%
Northumbrian Water | GLADSTONE STREET (G1) | 6NW801297 | 253/A/0942 | 253/A/0942 |  | SO on sewer network | NZ2910015000 | GB103025072596 | Skerne from Demons Beck to Tees | SKERNE |  |  | Commissioned pre-2016 - full year data expected | 4.75 | 11 | 97.34%
Northumbrian Water | GLASSHOUSE STREET PS | 6NW800546 | 235/1767 | 235/1767 | 235/1767-01 | Storm discharge at pumping station | NZ2713063480 | GB510302310200 | TYNE | RIVER TYNE SALINE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 1015.5 | 149 | 95.85% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | GLAXO WEST CSO | 6NW801322 | 225/1025 | 225/1025 |  | SO on sewer network | NZ2900185382 | GB103022077062 | Wansbeck from Bothal Burn to North Sea | RIVER WANSBECK (SALINE ESTUAR) |  |  | Commissioned pre-2016 - full year data expected | 55.75 | 28 | 79.22% | Sensor failure / issue | Resolved - July | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution
Northumbrian Water | GLEBE ESTATE CSO | 6NW801511 | 255/1124 | 255/1124 |  | SO on sewer network | NZ4068050390 | 367 | #N/A | SEATON BURN |  |  | Commissioned pre-2016 - full year data expected | 2.75 | 7 | 97.97%
Northumbrian Water | MANOR ROAD CSO GLENDALE AVENUE | 6NW801368 | 235/1952 | 235/1952 |  | SO on sewer network | NZ3102057947 | GB103023075690 | Don from Source to Tidal Limit | DON |  |  | Commissioned pre-2016 - full year data expected | 98.5 | 27 | 99.92%
Northumbrian Water | GLENTOWER GROVE SPS | 6NW800431 | 255/5046 | 255/5046 | A1 | Storm discharge at pumping station | NZ5175029930 | 368 | #N/A | UNNAMED COASTAL STREAM |  | Seaton Carew (North) | Commissioned in 2018 - full year data expected | 13.6 | 2 | 99.98%
Northumbrian Water | GOATSBECK TERRACE CSO | 6NW801178 | 244/0947 | 244/0947 |  | SO on sewer network | NZ2490140081 | GB103024077552 | Browney from Deerness confl to Wear | GOATS BECK (RIVER BROWNEY) |  |  | Commissioned pre-2016 - full year data expected | 1 | 2 | 99.99%
Northumbrian Water | GOLDEN LION SPS | 6NW800181 | 245/1169 | 245/1169 | A1 | Storm discharge at pumping station | NZ3488956750 | GB510302402900 | WEAR | WEAR ESTUARY |  |  | Commissioned in 2020 - full year data expected | 230.5422 | 37 | 100%
Northumbrian Water | GOLF COURSE ROAD CSO | 6NW801410 | 245/1369 | 245/1369 |  | SO on sewer network | NZ3231051790 | GB103024077630 | Herrington Burn from Source to Lumley Park Burn | HERRINGTON BURN |  |  | Commissioned pre-2016 - full year data expected | 1.25 | 2 | 99.96%
Northumbrian Water | GOMER TCE SSO | 6NW801105 | 241/1056 | 241/1056 |  | SO on sewer network | NZ2065030350 | GB103024077463 | Wear from Beechburn Beck to Gaunless | WEAR |  |  | Commissioned pre-2016 - full year data expected | 10.5 | 9 | 90.44%
Northumbrian Water | GRANGE BANK CSO | 6NW801044 | 241/1141 | 241/1141 |  | SO on sewer network | NZ1731031590 | GB103024077390 | Beechburn Beck (Trib of Wear) | BEECHBURN BECK |  |  | Commissioned pre-2016 - full year data expected | 15.25 | 12 | 99.99%
Northumbrian Water | GRANGE MILL CSO | 6NW801645 | #TBC | Permit Anomaly | To be permitted for storm | SO on sewer network | NZ5521210177 | GB103025071890 | Leven from Source to Tame | River Leven |  |  | Commissioned pre-2016 - full year data expected | 44.5 | 19 | 99.99%
Northumbrian Water | GRANGE PARK CSO (WK016) | 6NW801320 | 226/1265 | 226/1265 |  | SO on sewer network | NZ2824083613 | 5 | #N/A | THE SLEEK BURN |  |  | Commissioned pre-2016 - full year data expected | 767 | 86 | 99.98% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | SHILBOTTLE CSO A GRANGE ROAD | 6NW800858 | 223/G/0088 | 223/G/0088 |  | SO on sewer network | NU1980008740 | GB103022076720 | Tyelaw Burn Catchment (trib of Coquet) | TYELAW BURN |  |  | Commissioned pre-2016 - full year data expected | 0.75 | 2 | 99.99%
Northumbrian Water | GRANGE VILLA CSO | 6NW800162 | 245/1214 | 245/1214 |  | SO on sewer network | NZ2385052050 | GB103024077590 | Twizell Burn from Source to Cong Burn | BLINDY BURN (TWIZZEL BURN) |  |  | Commissioned in 2016 - full year data expected | 39 | 5 | 97.23%
Northumbrian Water | GRANGEFIELD ROAD SSO | 6NW801540 | 25/04/1627 | 25/04/1627 |  | SO on sewer network | NZ4340019200 | GB103025072550 | Lustrum Beck Catchment (trib of Tees) | LUSTRUM BECK |  |  | Commissioned pre-2016 - full year data expected | 15.75 | 11 | 99.77%
Northumbrian Water | GRANVILLE TCE SSO | 6NW800440 | 256/1068 | 256/1068 |  | SO on sewer network | NZ6165025250 | GB650301500005 | Tees Coastal | NORTH SEA |  | Redcar Sands - Granville Terrace | Commissioned in 2020 - full year data expected | 444.8667 | 72 | 99.98%
Northumbrian Water | GRASSBANKS CSO | 6NW801343 | 235/A/0510 | 235/A/0510 |  | SO on sewer network | NZ3060059900 | GB103023075690 | Don from Source to Tidal Limit | DON |  |  | Commissioned pre-2016 - full year data expected | 11 | 3 | 99.98%
Northumbrian Water | GRASSHOLM PLACE CSO | 6NW801251 | 235/1896 | 235/1896 |  | SO on sewer network | NZ2613769185 | GB103023075780 | Ouse Burn from Source to Tyne | OUSE BURN |  |  | Commissioned pre-2016 - full year data expected | 472.5 | 52 | 96.29% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | GRAY LANE STORM SEWAGE OVERFLOW | 6NW800925 | 252/1053 | 252/1053 |  | SO on sewer network | NZ0491015990 | GB103025072512 | Tees from Percy Beck to River Greta | TEES |  |  | Commissioned pre-2016 - full year data expected | 37 | 28 | 91.66%
Northumbrian Water | GRAYS ROAD CSO | 6NW801541 | 25/04/1661 | 25/04/1661 |  | SO on sewer network | NZ4349019453 | GB103025072550 | Lustrum Beck Catchment (trib of Tees) | LUSTRUM BECK |  |  | Commissioned pre-2016 - full year data expected | 3.5 | 5 | 98.63%
Northumbrian Water | GRAYS ROAD CSO | 6NW800414 | 25/04/1628 | 25/04/1628 |  | SO on sewer network | NZ4348319360 | GB103025072550 | Lustrum Beck Catchment (trib of Tees) | LUSTRUM BECK |  |  | Commissioned in 2017 - full year data expected | 689.5 | 64 | 99.97% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | GRAYTHORP STW | 6NW800195 | 25/04/1758 | 25/04/1758 | 25/04/1758-02 | Inlet SO at WwTW | NZ5215026980 | GB510302509900 | TEES | UNNAMED TRIB OF SEATON CHANNEL |  |  | Commissioned in 2020 - full year data expected | 2112.0158 | 157 | 100%
Northumbrian Water | GREAT AYTON STW | 6NW800801 | 25/04/1859 | 25/04/1859 | A2 | Storm tank at WwTW | NZ5469309700 | GB103025071890 | Leven from Source to Tame | RIVER LEVEN |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | GREAT BROUGHTON & KIRBY CSO MH6 | 6NW801593 | 254/E/0277 | 254/E/0277 |  | SO on sewer network | NZ5439206848 | GB103025071870 | Broughton Beck from Source to River Leven | BROUGHTON BECK |  |  | Commissioned pre-2016 - full year data expected | 24.5 | 18 | 99.78% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | GREAT BROUGHTON STW | 6NW800800 | 25/04/1676 | 25/04/1676 | A2 | Storm tank at WwTW | NZ5412007120 | GB103025071870 | Broughton Beck from Source to River Leven | RIVER LEVEN |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | GREATHAM STW CSO INLET | 6NW800193 | 25/04/1858 | 25/04/1858 | 25/04/1858-05 | Inlet SO at WwTW | NZ4925027200 | GB103025076030 | Greatham Beck Catchment (trib of Tidal Tees) | GREATHAM BECK |  |  | Feb 2021 | 33.7319 | 24 | 100%
Northumbrian Water | GREATHAM STW Storm Tank | 6NW800798 | 25/04/1858 | 25/04/1858 | 25/04/1858-04 | Storm tank at WwTW | NZ4925027200 | GB103025076030 | Greatham Beck Catchment (trib of Tidal Tees) | GREATHAM BECK |  |  | Commissioned in 2020 - full year data expected | 804.7903 | 95 | 100%
Northumbrian Water | GREEN BRIDGE CSO (DER 137) | 6NW800233 | 234/1110 | 234/1110 |  | SO on sewer network | NZ0907453027 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | DERWENT |  |  | Commissioned in 2019 - full year data expected | 101.0031 | 26 | 100%
Northumbrian Water | GREEN CRESCENT CSO (NTY 006) | 6NW801215 | 226/1255 | 226/1255 |  | SO on sewer network | NZ2567873505 | GB103022076190 | Seaton Burn from Source to Tidal Limit | SEATON BURN |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | GREEN LANE CSO 9(WK 008) | 6NW801295 | 225/1069 | 225/1069 |  | SO on sewer network | NZ2730086570 | GB103022077062 | Wansbeck from Bothal Burn to North Sea | WANSBECK, TRIBUTARY OF |  |  | Commissioned pre-2016 - full year data expected | 136.75 | 33 | 99.9%
Northumbrian Water | GREENFORD ROAD C18-102 | 6NW801676 | #TBC | Permit Anomaly | To be permitted for storm | SO on sewer network | NZ2929963167 | 8 | #N/A | River Tyne |  |  | Commissioned pre-2016 - full year data expected | 2.75 | 3 | 99.63%
Northumbrian Water | GREENHEAD PS | 6NW800485 | 232/0987 | 232/0987 | 232/0987-01 | Storm discharge at pumping station | NY6607065170 | GB103023075580 | Tipalt Burn from Source to South Tyne | TIPALT BURN |  |  | Commissioned in 2020 - full year data expected | 216.0306 | 31 | 99.97%
Northumbrian Water | GREEN'S LANE CSO | 6NW801529 | 254/E/0361 | 254/E/0361 |  | SO on sewer network | NZ4225718333 | GB103025072550 | Lustrum Beck Catchment (trib of Tees) | GREEN'S BECK |  |  | Commissioned pre-2016 - full year data expected | 2.25 | 7 | 98.27%
Northumbrian Water | GREENSIDE CSO | 6NW801002 | EPRBB3791AL | EPRBB3791AL |  | SO on sewer network | NZ1589665285 | 8 | #N/A | RIVER TYNE |  |  | Commissioned pre-2016 - full year data expected | 0.25 | 1 | 90.17%
Northumbrian Water | GRIBDALE TERRACE STW | 6NW800198 | 256/1062 | 256/1062 | A2 | Inlet SO at WwTW | NZ5844011060 | GB103025071890 | Leven from Source to Tame | RIVER LEVEN |  |  | Commissioned in 2017 - full year data expected | 49.5 | 16 | 99.98%
Northumbrian Water | GRINKLE ROAD CSO | 6NW800434 | 254/1912 | 254/1912 |  | SO on sewer network | NZ5873024080 | GB103025072320 | Tees Estuary (S Bank) | UNNAMED WATERCOUSE - TEES ESTU |  |  | Commissioned pre-2016 - full year data expected | 13.75 | 4 | 98.25%
Northumbrian Water | GROVE ROAD CSO M009 | 6NW800430 | 254/1851 | 254/1851 |  | SO on sewer network | NZ5079319593 | GB103025072210 | Marton West Beck Catchment (trib of Tidal Tees) | ORMESBY BECK |  |  | Commissioned pre-2016 - full year data expected | 25.75 | 22 | 98.76%
Northumbrian Water | GROVE TERRACE CSO DU005 | 6NW801198 | 244/1007 | 244/1007 |  | SO on sewer network | NZ2555040913 | GB103024077552 | Browney from Deerness confl to Wear | RIVER BROWNEY |  |  | Commissioned pre-2016 - full year data expected | 26.5 | 23 | 74.65% | Comms failure / issue | Resolved - July
Northumbrian Water | GUISBOROUGH STW | 6NW800439 | 25/06/1021 | 25/06/1021 | 25/06/1021-02 | SO on sewer network | NZ5998016180 | GB103025071970 | Skelton Beck Catch (Saltburn) trib of North Sea | CHAPEL BECK - HOWL BECK SYSTEM |  | Saltburn Pier | Commissioned in 2018 - full year data expected | 330.6678 | 31 | 100%
Northumbrian Water | CSO IN GUNNERGATE LANE | 6NW801580 | 25/04/1666 | 25/04/1666 |  | SO on sewer network | NZ5134015080 | GB103025072210 | Marton West Beck Catchment (trib of Tidal Tees) | MARTON WEST BECK |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 45.42% | Comms failure / issue | Scheduled
Northumbrian Water | GUNNERTON STW | 6NW800133(1) | 231/1078 | 231/1078 | 231/1078-03 | Inlet SO at WwTW | NY9039074970 | GB103023074880 | Gunnerton Burn from Source to N Tyne | GUNNERTON BURN |  |  | Feb 2021 | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | GUNNERTON STW | 6NW800133(2) | 231/1078 | 231/1078 | 231/1078-04 | Inlet SO at WwTW | NY9039074970 | GB103023074880 | Gunnerton Burn from Source to N Tyne | GUNNERTON BURN |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | HADSTON SEWAGE PUMPING STATION THE LADY BURN | 6NW800477(2) | 224/0990 | 224/0990 | 224/0990-01 - Consent Point 2 | Storm discharge at pumping station | NZ2757099140 | GB650301500001 | Northumberland South | NORTH SEA/LADY BURN |  | Druridge Bay North | Commissioned in 2020 - full year data expected | 604.4761 | 50 | 100%
Northumbrian Water | HADSTON SEWAGE PUMPING STATION THE North Sea | 6NW800477(1) | 224/0990 | 224/0990 | 224/0990-01 - Consent Point 1 | Storm discharge at pumping station | NZ2757099140 | GB650301500001 | Northumberland South | NORTH SEA/LADY BURN |  | Druridge Bay North | Commissioned in 2020 - full year data expected | 1518.4286 | 91 | 100%
Northumbrian Water | HAGGERSTON CASTLE CARAVAN PARK STW | 6NW800111 | 210/A/0849 | 210/A/0849 | 210/A/0849-02 | Inlet SO at WwTW | NU0524043560 | GB103021073222 | South Low from Haggerston Bridge to N Sea | SOUTH LOW |  |  | Commissioned in 2020 - full year data expected | 97.4067 | 18 | 53.49% | Comms failure / issue | Resolved - December
Northumbrian Water | HALL FARM CSO (SE037) | 6NW800289 | 243/0993 | 243/0993 |  | SO on sewer network | NZ2234334492 | GB103024077464 | Wear from Gaunless to Browney | WEAR TRIBUTARY |  |  | Commissioned pre-2016 - full year data expected | 52.5 | 22 | 99.99%
Northumbrian Water | MCLAREN DRIVE CSO HALL LODGE | 6NW800847 | 221/1003 | 221/1003 |  | SO on sewer network | NU1121033610 | GB103022076460 | Belford Burn from Source to Ross Low | BELFORD BURN (COASTAL STREAM) |  |  | Commissioned pre-2016 - full year data expected | 253.5 | 37 | 99.96%
Northumbrian Water | HALTON LEA GATE CSO | 6NW800872 | 232/G/0063 | 232/G/0063 |  | SO on sewer network | NY6553558679 | GB103023075531 | South Tyne from Black Burn to Tipalt Burn | BLACK BURN, TRIBUTARY OF |  |  | Commissioned pre-2016 - full year data expected | 35 | 19 | 99.94%
Northumbrian Water | HALTWHISTLE STW CSO INLET | 6NW800125 | 232/1098 | 232/1098 | 232/1098-03 | Inlet SO at WwTW | NY7159063720 | GB103023075570 | Haltwhistle Burn from Source to South Tyne | SOUTH TYNE / HALTWHISTLE BURN |  |  | Commissioned in 2020 - full year data expected | 221.2239 | 72 | 100%
Northumbrian Water | HALTWHISTLE STW Storm Tank | 6NW800698 | 232/1098 | 232/1098 | 232/1098-04 | Storm tank at WwTW | NY7159063720 | GB103023075570 | Haltwhistle Burn from Source to South Tyne | SOUTH TYNE / HALTWHISTLE BURN |  |  | Commissioned in 2020 - full year data expected | 593.6675 | 77 | 99.83%
Northumbrian Water | ESH WINNING CSO POINT A2 STAGS HEAD Hamilton Row | 6NW801046 | 244/E/0308 | 244/E/0308 |  | SO on sewer network | NZ1791140579 | GB103024077270 | Deerness from Source to Hedleyhope Burn | River Deerness |  |  | Commissioned pre-2016 - full year data expected | 177.25 | 29 | 97.06%
Northumbrian Water | HAMSTERLEY COLLIERY PS | 6NW800506 | 234/F/0368 | 234/F/0368 | 234/F/0368 (Storm Sewage) | SO on sewer network | NZ1253056800 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | DERWENT |  |  | Commissioned in 2017 - full year data expected | 476.75 | 55 | 99.93% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | HAMSTERLEY CSO | 6NW800973 | 241/C/0419 | 241/C/0419 |  | SO on sewer network | NZ1209030820 | GB103024072720 | Linburn Beck from Source to Wear | LINBURN BECK, TRIBUTARY OF |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.07%
Northumbrian Water | HAMSTERLEY MILL PUMPING STATION | 6NW800999 | 234/1084 | 234/1084 | 234/1084-01 | Storm discharge at pumping station | NZ1442056620 | GB103023074780 | Pont Burn Catchment (trib of Derwent) | PONT BURN (RIVER DERWENT) |  |  | Commissioned pre-2016 - full year data expected | 381.75 | 63 | 98.88% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | HAMSTERLEY STW | 6NW800722 | 241/1147 | 241/1147 | 241/1147-02 | Storm tank at WwTW | NZ1214030660 | GB103024072720 | Linburn Beck from Source to Wear | LINBURN BECK |  |  | Commissioned in 2020 - full year data expected | 267.9661 | 41 | 89.54% | Installation set-up/design issue | Resolved - March
Northumbrian Water | HARBOTTLE SEWAGE TREATMENT WORKS | 6NW800105 | 223/0990 | 223/0990 | A2 | Inlet SO at WwTW | NT9384004630 | GB103022076691 | Coquet from Usway Burn to Holystone Burn | RIVER COQUET |  |  | Commissioned in 2020 - full year data expected | 633.9158 | 100 | 99.96%
Northumbrian Water | HARBOUR SPS | 6NW800466 | 221/0914 | 221/0914 | A1 | Storm discharge at pumping station | NU2196032260 | GB650301440000 | Northumberland North | NORTH SEA |  | Seahouses North | Commissioned in 2018 - full year data expected | 1.5456 | 2 | 49.22% | Comms failure / issue | N/A - Ongoing investigation
Northumbrian Water | HARROWGATE HILL SEWAGE PS | 6NW800560 | 253/1276 | 253/1276 | 253/1276-01 | Storm discharge at pumping station | NZ2951017810 | GB103025072596 | Skerne from Demons Beck to Tees | SKERNE, TRIBUTARY OF |  |  | Commissioned in 2020 - full year data expected | 8.6547 | 11 | 100%
Northumbrian Water | HARTFORD BRIDGE SEWAGE PUMPING STAN | 6NW800549 | 226/1248 | 226/1248 | 226/1248-01 | Storm discharge at pumping station | NZ2430079990 | GB103022077052 | Blyth from Pont to Tidal Limit | RIVER BLYTH |  |  | Commissioned in 2020 - full year data expected | 43.8208 | 4 | 100%
Northumbrian Water | HARTLEY CARAVAN PARK PS | 6NW800594 | 226/1090 | 226/1090 | 226/1090-02 | Storm discharge at pumping station | NZ3440075810 | GB650301500002 | Tyne and Wear | NORTH SEA |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | HARTON LOW STAITHES CSO | 6NW801477 | 235/1908 | 235/1908 |  | SO on sewer network | NZ3592067100 | GB510302310200 | TYNE | TYNE SALINE ESTUARY |  |  | Commissioned in 2020 - full year data expected | 171.4267 | 40 | 100%
Northumbrian Water | HARTON LOW STAITHES (MILL DAM) CSO | 6NW801476 | 235/1907 | 235/1907 |  | SO on sewer network | NZ3584066910 | GB510302310200 | TYNE | TYNE SALINE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 2 | 3 | 99.48%
Northumbrian Water | HARWAL ROAD CSO (REF. L16) | 6NW801604 | 25/04/1782 | 25/04/1782 |  | SO on sewer network | NZ5905024858 | GB103025072320 | Tees Estuary (S Bank) | FLEET BECK |  |  | Commissioned pre-2016 - full year data expected | 81.5 | 28 | 99.86%
Northumbrian Water | HASWELL SSO | 6NW801493 | 255/E/0643 | 255/E/0643 |  | SO on sewer network | NZ3870041700 | GB103024077540 | Pittington Beck from Coalford to Old Durham Beck | COLDWELL BURN/MURTON DENE |  |  | Commissioned pre-2016 - full year data expected | 82.25 | 27 | 96.55%
Northumbrian Water | HAUGH LANE CSO | 6NW800254 | 233/1224 | 233/1224 |  | SO on sewer network | NZ1711464192 | 8 | #N/A | TRIB RIVER TYNE |  |  | Mar 2021 | 35.5481 | 8 | 99.7%
Northumbrian Water | HAWTHRON CSO | 6NW801533 | 255/E/0640 | 255/E/0640 |  | SO on sewer network | NZ4216745839 | GB103025075950 | Hawthorn Burn from Source to North Sea | NORTH DENE BURN |  |  | Commissioned pre-2016 - full year data expected | 132.25 | 54 | 92.08%
Northumbrian Water | HAWTHORNE CLOSE STORAGE TANK | 6NW801500 | 255/1180 | 255/1180 |  | SO on sewer network | NZ3986046655 | GB103025075970 | Dalton Beck to North Sea | DALTON BURN |  |  | Commissioned pre-2016 - full year data expected | 5.5 | 3 | 97.55%
Northumbrian Water | HAY STREET CSO SU056 | 6NW801504 | 245/1374 | 245/1374 |  | SO on sewer network | NZ3953357455 | GB510302402900 | WEAR | WEAR (SALINE ESTUARY) |  |  | Commissioned pre-2016 - full year data expected | 18.25 | 22 | 98.23%
Northumbrian Water | HAYDON BRIDGE STW | 6NW800702 | 232/1165 | 232/1165 | A2 | Storm tank at WwTW | NY8502064750 | GB103023075710 | South Tyne from Allen to North Tyne | RIVER SOUTH TYNE |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | HEADLAM SPS | 6NW800511 | 252/1002 | 252/1002 | A1 | Storm discharge at pumping station | NZ1782018580 | GB103025072300 | Piercebridge Beck from Source to Tees | LANGTON BECK (TEES) |  |  | Commissioned in 2020 - full year data expected | 0.12194 | 3 | 98.92%
Northumbrian Water | HEATON CSO CORNEL RD | 6NW800326 | EPRCB3192VE | EPRCB3192VE |  | SO on sewer network | NZ2902666550 | GB103023075760 | Wallsend Burn (Trib of Tyne) | WALLSEND BURN |  |  | Commissioned in 2020 - full year data expected | 60.25 | 35 | 88.11% | Comms failure / issue | N/A - Ongoing investigation
Northumbrian Water | HEATON GARDENS PUMPING STATION | 6NW800600 | 235/1388 | 235/1388 | A | Storm discharge at pumping station | NZ3551062520 | GB103023075690 | Don from Source to Tidal Limit | RIVER DON |  |  | EDM to be installed by December 2023 | #N/A | #N/A | #N/A
Northumbrian Water | HEDDON BANKS FARM CSO | 6NW800995 | 233/1237 | 233/1237 |  | SO on sewer network | NZ1330066400 | 8 | #N/A | TYNE |  |  | Commissioned pre-2016 - full year data expected | 20 | 19 | 99.99%
Northumbrian Water | HEDDON ON THE WALL STW | 6NW800728 | 233/1266 | 233/1266 | A2 | Storm tank at WwTW | NZ1378065580 | GB510302310200 | TYNE | TYNE |  |  | Commissioned in 2020 - full year data expected | 14.1672 | 21 | 46.69% | Comms failure / issue | Resolved - July
Northumbrian Water | HEIGHINGTON CSO | 6NW801192 | 25/03/1240 | 25/03/1240 |  | SO on sewer network | NZ2519021910 | GB103025072596 | Skerne from Demons Beck to Tees | DENE BECK (SKERNE CATCHMENT) |  |  | Commissioned pre-2016 - full year data expected | 26.25 | 18 | 99.32%
Northumbrian Water | HENDON PRELIMINARY TREATMENT WORKS | 6NW800185 | 245/1213 | 245/1213 | 245/1213-01 | Inlet SO at WwTW | NZ4108056150 | GB650301500002 | Tyne and Wear | NORTH SEA |  |  | Commissioned in 2020 - full year data expected | 565.435 | 116 | 100%
Northumbrian Water | HEPPLE SEWAGE TREATMENT WORKS | 6NW800106 | 223/0995 | 223/0995 | 223/0995-02 | Inlet SO at WwTW | NT9890000250 | GB103022076692 | Coquet from Holystone Burn to Forest Burn | RIVER COQUET |  |  | Commissioned in 2020 - full year data expected | 51.0033 | 6 | 68.78% | Comms failure / issue | Resolved - August
Northumbrian Water | HEPSCOTT SEWAGE TREATMENT WORKS | 6NW800811 | 226/1281 | 226/1281 | A2 | Storm tank at WwTW | NZ2283083810 | GB103022076230 | Sleek Burn / Hepscott Burn Source to Tidal Limit | HEPSCOTT BURN |  |  | Mar 2021 | 339.5833 | 42 | 98.64%
Northumbrian Water | WEST PARK ESTATE CSO | 6NW000004 | 245/1301 | 245/1301 |  | SO on sewer network | NZ3558853076 | GB103024077630 | Herrington Burn from Source to Lumley Park Burn | HERRINGTON BURN VIA A CULVERT |  |  | Commissioned pre-2016 - full year data expected | 2.25 | 6 | 99.99%
Northumbrian Water | HETTON-LE-HOLE SSO NO. 1 | 6NW801462 | 245/1365 | 245/1365 |  | SO on sewer network | NZ3506047230 | GB103024077580 | Lumley Park Burn from Source to Herrington Burn | HETTON BURN |  |  | Commissioned pre-2016 - full year data expected | 15.25 | 13 | 99.99%
Northumbrian Water | HETTON PARK BOWLING GREEN CSO | 6NW801463 | 245/1364 | 245/1364 |  | SO on sewer network | NZ3507247840 | GB103024077580 | Lumley Park Burn from Source to Herrington Burn | HETTON BURN |  |  | Commissioned pre-2016 - full year data expected | 33.5 | 23 | 99.26%
Northumbrian Water | HETTON-LE-HOLE SSO NO. 3 | 6NW801447 | 245/1362 | 245/1362 |  | SO on sewer network | NZ3494048180 | GB103024077580 | Lumley Park Burn from Source to Herrington Burn | HETTON BURN |  |  | Commissioned pre-2016 - full year data expected | 32.5 | 17 | 99.71%
Northumbrian Water | HETTON ROAD CSO SU33 | 6NW801446 | 245/1361 | 245/1361 |  | SO on sewer network | NZ3458748641 | GB103024077580 | Lumley Park Burn from Source to Herrington Burn | ROUGH DENE BURN |  |  | Commissioned pre-2016 - full year data expected | 204.75 | 56 | 90.38% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | THE LARCHES P.S. | 6NW800494 | 233/1042 | 233/1042 | 233/1042-01 | Storm discharge at pumping station | NY9284063840 | GB103023075801 | Tyne from Watersmeet to Tidal Limit | COCKSHAW BURN |  |  | Commissioned in 2020 - full year data expected | 29.8781 | 22 | 100%
Northumbrian Water | HEXHAM CSO LEAZES TERRACE | 6NW800224 | EPRBB3598RX | EPRBB3598RX |  | SO on sewer network | NY9284664073 | GB103023075801 | Tyne from Watersmeet to Tidal Limit | CULVERTED TRIB COCKSHAW BURN |  |  | Commissioned in 2020 - full year data expected | 15.25 | 18 | 82.73% | Comms failure / issue | Resolved - March
Northumbrian Water | HEXHAM STW | 6NW800706 | 233/1281 | 233/1281 | A2 | Storm tank at WwTW | NY9487064130 | GB103023075801 | Tyne from Watersmeet to Tidal Limit | TYNE |  |  | Commissioned in 2020 - full year data expected | 1301.5619 | 128 | 99.99%
Northumbrian Water | HIGH CARR ROAD CSO | 6NW801230 | 245/1300 | 245/1300 |  | SO on sewer network | NZ2649144069 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | WEAR, TRIBUTARY OF |  |  | Commissioned pre-2016 - full year data expected | 320.6333 | 109 | 99.58% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | HIGH FRIARSIDE CSO | 6NW801028 | 234/A/0590 | 234/A/0590 |  | SO on sewer network | NZ1568557297 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | DERWENT, TRIBUTARY OF |  |  | Commissioned pre-2016 - full year data expected | 85.5 | 22 | 91.26%
Northumbrian Water | HIGH HAUXLEY PS | 6NW800541 | 224/0947 | 224/0947 | 224/0947-01 | Storm discharge at pumping station | NU2762003050 | 362 | #N/A | BONDICARR BURN TRIB |  |  | Commissioned in 2020 - full year data expected | 143.1103 | 26 | 99.42%
Northumbrian Water | WARREN HOUSE SEA OUTFALL HIGH RELIEF | 6NW800187 | 255/1158 | 255/1158 |  | Inlet SO at WwTW | NZ4435042600 | 367 | #N/A | WARREN HOUSE BURN |  |  | Commissioned in 2020 - full year data expected | 0 | 0 | 96.21%
Northumbrian Water | HIGH SPEN CSO STROTHERS ROAD | 6NW800993 | EPRBB3897RH | EPRBB3897RH |  | SO on sewer network | NZ1388960211 | GB103023074791 | Blaydon Burn | A TRIBUTARY OF BARLOW BURN |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | HIGH SPEN CSO ROWLANDS GILL 6 | 6NW800992 | EPRBB3897WE | EPRBB3897WE |  | SO on sewer network | NZ1377259658 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | UNNAMED TRIB OF SPEN BURN |  |  | Commissioned pre-2016 - full year data expected | 1 | 2 | 95.97%
Northumbrian Water | HIGH SPEN PUMPING STATION | 6NW800507 | 233/1162 | 233/1162 | 233/1162-01 | Storm discharge at pumping station | NZ1404060600 | GB103023074791 | Blaydon Burn | BARLOW BURN |  |  | Commissioned in 2020 - full year data expected | 194.1503 | 38 | 99.71%
Northumbrian Water | HIGH ST CSO | 6NW801363 | 245/1155 | 245/1155 |  | SO on sewer network | NZ3076044630 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | WEAR TRIB |  |  | Commissioned pre-2016 - full year data expected | 4.25 | 8 | 99.98%
Northumbrian Water | HIGH STREET CSO | 6NW801594 | EPRCB3190WC | EPRCB3190WC |  | SO on sewer network | NZ5439206848 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | BROUGHTON BECK |  |  | Commissioned pre-2016 - full year data expected | 0.5 | 1 | 99.99%
Northumbrian Water | HIGH WEST STREET CSO (G066) | 6NW801211 | 235/1927 | 235/1927 |  | SO on sewer network | NZ2519163597 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 140.3667 | 64 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | HIGH WATERHOUSE FARM (100M WEST OF) | 6NW801061 | 244/1018 | 244/1018 |  | SO on sewer network | NZ1850440808 | GB103024077270 | Deerness from Source to Hedleyhope Burn | DEERNESS |  |  | Commissioned pre-2016 - full year data expected | 319.25 | 45 | 96.04%
Northumbrian Water | HILLS SEWAGE PUMPING STATION | 6NW800421 | 254/0047 | 254/0047 |  | SO on sewer network | NZ4441520459 | GB103025072550 | Lustrum Beck Catchment (trib of Tees) | LUSTRUM BECK, TRIBUTARY OF |  |  | Commissioned in 2020 - full year data expected | 458.7619 | 69 | 81.11% | Sensor failure / issue | Resolved - March
Northumbrian Water | HILTON PS | 6NW800641 | 254/1963 | 254/1963 | 254/1963-01 | Storm discharge at pumping station | NZ4704010860 | GB103025071880 | Leven from Tame to River Tees | BREWSDALE BECK (LEVEN) |  |  | Commissioned in 2020 - full year data expected | 22.8147 | 7 | 100%
Northumbrian Water | HOBDALE HOUSE CSO | 6NW801619 | 256/1074 | 256/1074 |  | SO on sewer network | NZ6610017601 | GB103025071960 | Saltburn Gill Catch trib of North Sea | BOOS BECK-TRIB OF SALTBURN BK |  |  | Commissioned pre-2016 - full year data expected | 4 | 11 | 99.93%
Northumbrian Water | HOLLINSIDE SEWAGE DISPOSAL WORKS | 6NW800154 | 244/C/0282 | 244/C/0282 |  | Inlet SO at WwTW | NZ1607046140 | GB103024077320 | Browney from Pan Burn to Smallhope Burn | BROWNEY, TRIBUTARY OF |  |  | Mar 2021 | 1.1297 | 7 | 99.47%
Northumbrian Water | HOLYHILL GARDENS EAST CSO | 6NW801643 | 245/1075 | 245/1075 |  | SO on sewer network | NZ2035251914 | GB103024077590 | Twizell Burn from Source to Cong Burn | STANLEY BURN |  |  | Commissioned pre-2016 - full year data expected | 346 | 66 | 99.97% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | HOLMHILL FIELD CSO CH043 | 6NW800332 | NPSWQD009250 | NPSWQD009250 |  | SO on sewer network | NZ2718349283 | GB103024077623 | South Burn to confluence with Wear | TRIB OF SOUTH BURN RIVER WEAR |  |  | Commissioned pre-2016 - full year data expected | 160 | 45 | 98.78%
Northumbrian Water | HOLY ISLAND STW | 6NW800116 | 221/1016 | 221/1016 | 221/1016-03 | Inlet SO at WwTW | NU1413041940 | GB650301440000 | Northumberland North | NORTH SEA |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | HOLYWELL HOUSE (CSO) | 6NW801397 | 226/1186 | 226/1186 |  | SO on sewer network | NZ3123072640 | GB103022076180 | Brierdene Burn from Source to North Sea | BRIERDENE BURN (COASTAL STREA) |  |  | Commissioned pre-2016 - full year data expected | 29 | 5 | 83.89% | Sensor failure / issue | Resolved - December
Northumbrian Water | HOLYWELL P.S. | 6NW800589 | 226/0947 | 226/0947 | A | Storm discharge at pumping station | NZ3250074650 | GB103022076190 | Seaton Burn from Source to Tidal Limit | SEATON BURN |  |  | Commissioned in 2020 - full year data expected | 10.5564 | 5 | 99.98%
Northumbrian Water | HOPGARTH GARDENS CSO | 6NW801281 | 245/1268 | 245/1268 |  | SO on sewer network | NZ2778551535 | GB103024077600 | Cong Burn from Twizell Burn to Wear | CONG BURN |  |  | Commissioned pre-2016 - full year data expected | 20.75 | 20 | 99.35%
Northumbrian Water | EASINGTON OUTFALL HORDEN DENE SPS | 6NW800627 | 255/1146 | 255/1146 | 255/1146-01 | Storm discharge at pumping station | NZ4456043620 | GB650301500002 | Tyne and Wear | NORTH SEA |  |  | Commissioned in 2020 - full year data expected | 498.1422 | 82 | 100%
Northumbrian Water | HORDEN STW | 6NW800186 | 255/1145 | 255/1145 | 255/1145-03 | Inlet SO at WwTW | NZ4577043310 | GB650301500002 | Tyne and Wear | NORTH SEA |  |  | Commissioned pre-2016 - full year data expected | 1.5 | 4 | 99.89%
Northumbrian Water | HORNCLIFFE NORTH STW No 1 | 6NW800815 | 210/0887 | 210/0887 | 210/0887-02 | Inlet SO at WwTW | NT9267849961 | 3 | #N/A | TWEED |  |  | Commissioned pre-2016 - full year data expected | 0.75 | 3 | 99.99%
Northumbrian Water | HORNCLIFFE NORTH STW No 2 | 6NW800816 | 210/0887 | 210/0887 | 210/0887-02 | Inlet SO at WwTW | NT9267849961 | 3 | #N/A | TWEED |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | HOUGHTON LE SPRING CSO | 6NW801431 | EPRBB3899VA | EPRBB3899VA |  | SO on sewer network | NZ3336752470 | GB103024077630 | Herrington Burn from Source to Lumley Park Burn | TRIB OF RIVER WEAR |  |  | Commissioned pre-2016 - full year data expected | 86.75 | 45 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | SOUTH LEIGH CSO HOUGHWELL HOUSE | 6NW801065 | 235/1711 | 235/1711 |  | SO on sewer network | NZ1908053957 | GB103023075670 | Team from Source to Tyne | HOUGHWELL BURN |  |  | Commissioned pre-2016 - full year data expected | 81.5 | 28 | 99.79%
Northumbrian Water | HOWDON ROAD CSO (NTY 040) | 6NW800382 | 235/1899 | 235/1899 |  | SO on sewer network | NZ3548567147 | 8 | #N/A | RIVER TYNE |  |  | Commissioned in 2018 - full year data expected | 12.75 | 11 | 99.99%
Northumbrian Water | CONSETT IRON WORKS HOWDON WOOD CSO | 6NW800945 | 234/F/0400 | 234/F/0400 |  | SO on sewer network | NZ0900051000 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | HOWDEN BURN |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 97.16%
Northumbrian Water | HOWDON (ADJACENT A19 ROUNDABOUT)CSO | 6NW800366 | NPSWQD009134 | NPSWQD009134 |  | SO on sewer network | NZ3300666078 | GB510302310200 | TYNE | THE RIVER TYNE |  |  | Commissioned in 2019 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | HOWDON STW CSO INLET | 6NW800200 | 235/1804 | 235/1804 | 235/1804-01 | Inlet SO at WwTW | NZ3370566132 | 8 | #N/A | River Tyne |  |  | Commissioned in 2020 - full year data expected | 14.7656 | 14 | 100%
Northumbrian Water | HOWDON STW CSO INLET NORTH BANK | 6NW800178 | 235/1695 | 235/1695 | 235/1695-03 | Inlet SO at WwTW | NZ3370066130 | GB510302310200 | TYNE | RIVER TYNE SALINE ESTUARY |  |  | Commissioned in 2020 - full year data expected | 882.0142 | 86 | 100%
Northumbrian Water | HOWDON STW CSO INLET South BANK | 6NW800179 | 235/1695 | 235/1695 | 235/1695-05 | Inlet SO at WwTW | NZ3370066130 | GB510302310200 | TYNE | RIVER TYNE SALINE ESTUARY |  |  | Commissioned in 2020 - full year data expected | 1427.4475 | 136 | 100%
Northumbrian Water | HOWDON STW CSO Primary treated storm | 6NW801682 | 235/1695 | 235/1695 | 235/1695-07 | Inlet SO at WwTW | NZ3370066130 | GB510302310200 | TYNE | RIVER TYNE SALINE ESTUARY |  |  | Commissioned in 2020 - full year data expected | 2087.2931 | 162 | 100%
Northumbrian Water | HOWLING LANE CSO A046 | 6NW800853 | 222/0861 | 222/0861 |  | SO on sewer network | NU1825013518 | GB103022076350 | Aln from Edlingham Burn to Tidal Limit | WASH BURN |  |  | Commissioned pre-2016 - full year data expected | 85.25 | 52 | 99.38% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | HUGHBOURNE STREET CSO | 6NW801670 | #TBC | Permit Anomaly | To be permitted for storm | SO on sewer network | NZ2960382325 | 5 | #N/A | River Blyth |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | HUMSHAUGH STW | 6NW800136 | 231/1108 | 231/1108 | A2 | Inlet SO at WwTW | NY9216070690 | GB103023075802 | N Tyne from Barrasford to S Tyne confluence | NORTH TYNE |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | HUNTSHIELD FORD CSO | 6NW800890 | 241/1157 | 241/1157 |  | SO on sewer network | NY8886738132 | GB103024077440 | Wear from Wearhead to Middlehope Burn, Iresho | RIVER WEAR |  |  | Commissioned pre-2016 - full year data expected | 84.75 | 32 | 94.71%
Northumbrian Water | HUNWICK LANE CSO | 6NW801079 | 243/0994 | 243/0994 |  | SO on sewer network | NZ1935035140 | GB103024077464 | Wear from Gaunless to Browney | WILLINGTON BURN TRIBUTARY |  |  | Commissioned pre-2016 - full year data expected | 0.25 | 1 | 99.99%
Northumbrian Water | HURWORTH PLACE SPS | 6NW800556 | 254/1019 | 254/1019 | A1 | Storm discharge at pumping station | NZ2901709813 | GB103025072595 | Tees from Skerne to Tidal Limit | RIVER TEES |  |  | Commissioned in 2019 - full year data expected | 17.3292 | 14 | 100%
Northumbrian Water | HUSTLEDOWN ROAD CSO | 6NW801087 | 245/1257 | 245/1257 |  | SO on sewer network | NZ1949851638 | GB103024077590 | Twizell Burn from Source to Cong Burn | STANLEY BURN |  |  | Commissioned pre-2016 - full year data expected | 33.25 | 22 | 99.93%
Northumbrian Water | HUSTLEDOWN STW | 6NW800749 | 245/1247 | 245/1247 | A2 | Storm tank at WwTW | NZ2133151601 | GB103024077590 | Twizell Burn from Source to Cong Burn | TWIZELL BURN |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | HUTTON RUDBY SPS | 6NW800635 | 25/04/1643 | 25/04/1643 | A1 | Storm discharge at pumping station | NZ4698206573 | GB103025071880 | Leven from Tame to River Tees | RIVER LEVEN |  |  | Commissioned in 2020 - full year data expected | 396.0086 | 54 | 100%
Northumbrian Water | HUTTON RUDBY SEWAGE TREATMENT WORKS | 6NW800794 | 25/04/1751 | 25/04/1751 | A2 | Storm tank at WwTW | NZ4654006910 | GB103025071880 | Leven from Tame to River Tees | RIVER LEVEN |  |  | Commissioned in 2020 - full year data expected | 1661.9842 | 154 | 92.87%
Northumbrian Water | INGLEBY GREENHOW STW | 6NW800802 | 25/04/1740 | 25/04/1740 | 25/04/1740-03 | Storm tank at WwTW | NZ5788006510 | GB103025071870 | Broughton Beck from Source to River Leven | INGLEBY BECK (TO R.LEVEN) |  |  | Commissioned in 2020 - full year data expected | 672.9783 | 55 | 100%
Northumbrian Water | WALL SEWAGE TREATMENT WORKS | 6NW800135 | 231/A/0454 | 231/A/0454 |  | Inlet SO at WwTW (12xDWF) | NY9136068550 | GB103023075802 | N Tyne from Barrasford to S Tyne confluence | NORTH TYNE |  |  | Commissioned in 2020 - full year data expected | 0.12444 | 1 | 91.78%
Northumbrian Water | WALL SEWAGE TREATMENT WORKS | 6NW800134 | 231/A/0453 | 231/A/0453 |  | Inlet SO at WwTW (6-12 x DWF) | NY9139068533 | GB103023075802 | N Tyne from Barrasford to S Tyne confluence | River North Tyne |  |  | Commissioned in 2020 - full year data expected | 197.3575 | 70 | 91.78%
Northumbrian Water | CSO INLET AT BOWSDEN SEWAGE TREATMS | 6NW800108 | 210/1292 | 210/1292 |  | Inlet SO at WwTW | NT9973041910 | GB103021073221 | South Low from Source to Haggerston Bridge | BOWSDEN BURN |  |  | Commissioned in 2020 - full year data expected | 338.0811 | 84 | 100%
Northumbrian Water | INSTITUTE TERRACE CSO | 6NW801022 | #TBC | Permit Anomaly | To be permitted for storm | SO on sewer network | NZ1620737242 | GB103024077390 | Beechburn Beck (Trib of Wear) | Crook Beck |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | INTERNATIONAL PAINTS PUMPING STN. | 6NW800554 | 235/1751 | 235/1751 | 235/1751-01 | Storm discharge at pumping station | NZ2835062890 | GB510302310200 | TYNE | RIVER TYNE SALINE ESTUARY |  |  | Commissioned in 2020 - full year data expected | 135.3514 | 49 | 99.89%
Northumbrian Water | IVESTON LANE CSO | 6NW800998 | 244/0918 | 244/0918 |  | SO on sewer network | NZ1426050500 | GB103024077330 | Smallhope Burn from Source to Browney, Stocke | IVESTON BURN |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 75.58% | Comms failure / issue | Resolved - August
Northumbrian Water | JACKSON AVENUE CSO | 6NW801037 | NPSWQD010337 | NPSWQD010337 |  | SO on sewer network | NZ1668073450 | GB103022076860 | Pont from Med Burn to Small Burn | RIVER PONT |  |  | Commissioned pre-2016 - full year data expected | 370 | 41 | 99.99%
Northumbrian Water | JAMES STREET SSO | 6NW801584 | 25/04/1768 | 25/04/1768 |  | SO on sewer network | NZ5130020120 | 10 | #N/A | MIDDLE BECK (TEES) |  |  | Commissioned pre-2016 - full year data expected | 6.75 | 11 | 97.31%
Northumbrian Water | BLACKETT STREET JARROW | 6NW000005 | 235/1181 | 235/1181 |  | SO on sewer network | NZ3172065830 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 95 | 30 | 99.98%
Northumbrian Water | JARROW ROAD PUMPING STATION | 6NW800593 | 235/1405 | 235/1405 | A | Storm discharge at pumping station | NZ3490064850 | GB510302310200 | TYNE | DON ESTUARY |  |  | Commissioned in 2020 - full year data expected | 1090.4869 | 71 | 100%
Northumbrian Water | J F KENNEDY ESTATE CSO | 6NW801392 | 245/1302 | 245/1302 |  | SO on sewer network | NZ3182855951 | 9 | #N/A | WILLOWS POND |  |  | Commissioned pre-2016 - full year data expected | 3.0333 | 5 | 98.32%
Northumbrian Water | JOHN STREET CSO | 6NW801351 | 226/1058 | 226/1058 |  | SO on sewer network | NZ2960382326 | 5 | #N/A | BLYTH ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 1115.75 | 103 | 84.8% | Sensor failure / issue | Resolved - November | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | JOLLY FISHERMAN CSO | 6NW800217 | NPSWQD009505 | NPSWQD009505 |  | SO on sewer network | NU2589519892 | GB650301500001 | Northumberland South | NORTH SEA |  |  | Commissioned in 2020 - full year data expected | 0 | 0 | 39.15% | Access - Unable to retrieve data from non-telemetry data logger (NB: not to be used for delayed access to fix existing fault) | Scheduled
Northumbrian Water | JUBILEE PLACE CSO | 6NW801307 | 245/1299 | 245/1299 |  | SO on sewer network | NZ2859040730 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | WEAR |  |  | Commissioned pre-2016 - full year data expected | 1 | 2 | 99.86%
Northumbrian Water | JUBILEE ROAD CSO | 6NW800295 | 253/1109 | QC.25/03/1109 |  | SO on sewer network | NZ2381625646 | GB103025072400 | Woodham Burn from Source to Rushyford beck | TRIB OF RIVER SKERNE |  |  | Commissioned in 2017 - full year data expected | 35.75 | 25 | 99.99%
Northumbrian Water | JNC CHURCH ROAD/DOCK ROAD CSO | 6NW800828 | 210/1346 | 210/1346 |  | SO on sewer network | NT9965052330 | GB510202110000 | TWEED | RIVER TWEED (SALINE ESTUARY) |  | Spittal | Commissioned pre-2016 - full year data expected | 0 | 0 | 100%
Northumbrian Water | DAMSIDE AND STAITHES LANE CSO | 6NW801126 | 225/1072 | 225/1072 |  | SO on sewer network | NZ2012086080 | GB103022077061 | Wansbeck from Font to Bothal Burn | THE COTTING BURN |  |  | Commissioned pre-2016 - full year data expected | 281.5 | 34 | 97.55%
Northumbrian Water | CLAVERING RD & RUSKIN RD | 6NW000006 | 234/1144 | 234/1144 |  | SO on sewer network | NZ2006062130 | 8 | #N/A | DERWENT MILL RACE |  |  | Commissioned pre-2016 - full year data expected | 4.25 | 7 | 96.34%
Northumbrian Water | JUNC OF CLAVERING RD & SWALWEL BANK | 6NW801121 | 234/1143 | 234/1143 |  | SO on sewer network | NZ2006362126 | 8 | #N/A | DERWENT MILL RACE |  |  | Commissioned pre-2016 - full year data expected | 3.8 | 9 | 92.62%
Northumbrian Water | JUNCTION OF HEXHAM RD & | 6NW801122 | 234/1159 | 234/1159 |  | SO on sewer network | NZ2029062471 | GB510302310200 | TYNE | DERWENT (SALINE ESTUARY) |  |  | Commissioned pre-2016 - full year data expected | 302.1289 | 65 | 96.84% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | KELL GATE SSO | 6NW801566 | QR.25/04/1573 | QR.25/04/1573 |  | SO on sewer network | NZ4794013980 | GB103025072180 | Stainsby Beck Catchment (trib of Tidal Tees) | STAINTON BECK |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | KELLOE STW | 6NW800804 | 243/0965 | 243/0965 | 243/0965-03 | Storm tank at WwTW | NZ3383035890 | GB103024077410 | Croxdale Beck from Source to Wear | COXHOE BECK |  |  | Commissioned in 2020 - full year data expected | 294.3022 | 51 | 100%
Northumbrian Water | KENTON ROAD/ROCKERBY DRIVE CSO | 6NW800302 | 235/1549 | 235/1549 |  | SO on sewer network | NZ2422069510 | GB103023075780 | Ouse Burn from Source to Tyne | OUSE BURN |  |  | June 2021 | 0 | 0 | 99.8%
Northumbrian Water | KIER HARDY WAY | 6NW801495 | 245/1373 | 245/1373 |  | SO on sewer network | NZ3886158290 | GB510302402900 | WEAR | WEAR (SALINE ESTUARY) |  |  | Commissioned pre-2016 - full year data expected | 9.25 | 12 | 99.98%
Northumbrian Water | KILBURN ROAD CSO | 6NW801530 | 254/D/0407 | 254/D/0407 |  | SO on sewer network | NZ4293218548 | GB103025072550 | Lustrum Beck Catchment (trib of Tees) | GREENS BECK |  |  | Commissioned pre-2016 - full year data expected | 3.75 | 8 | 93.58%
Northumbrian Water | KILLINGWORTH WAGONWAY CSO | 6NW800360 | 235/1842 | 235/1842 |  | SO on sewer network | NZ3042767058 | GB103023075760 | Wallsend Burn (Trib of Tyne) | WALLSEND BURN |  |  | Commissioned pre-2016 - full year data expected | 83.25 | 34 | 84.51% | Comms failure / issue | Resolved - June
Northumbrian Water | KILTON MILL CSO | 6NW800446 | 256/C/0408 | 256/C/0408 |  | SO on sewer network | NZ7114919024 | GB103025071950 | Kilton Beck from Middle Gill Beck to North Sea | KILTON BECK |  |  | Commissioned in 2020 - full year data expected | 0.25 | 1 | 99.71%
Northumbrian Water | KIMBLESWORTH CSO | 6NW800324 | EPRBB3398RS | EPRBB3398RS |  | SO on sewer network | NZ2646447467 | GB103024077622 | Blackdene Burn to confluence with Wear | BLACKDENE BURN |  |  | July 2021 | 0 | 0 | 91.07%
Northumbrian Water | KING OSWY DRIVE CSO | 6NW801573 | 255/1117 | 255/1117 |  | SO on sewer network | NZ5001235871 | GB650301500005 | Tees Coastal | NORTH SEA |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.86%
Northumbrian Water | KING STREET SEWAGE PUMPING STATION | 6NW800469 | 221/1074 | 221/1074 | 221/1074-01 | Storm discharge at pumping station | NU2227031510 | 249 | #N/A | NORTH SEA |  |  | Commissioned in 2020 - full year data expected | 16.4947 | 21 | 99.59%
Northumbrian Water | KINGS ARMS LANE CSO | 6NW800880 | 232/1152 | 232/1152 |  | SO on sewer network | NY7174546573 | GB103023075531 | South Tyne from Black Burn to Tipalt Burn | TRIB RIVER NENT |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.78%
Northumbrian Water | KINGSMERE PS | 6NW800544 | 235/1886 | 235/1886 | 235/1886-01 | Storm discharge at pumping station | NZ2657055590 | GB103023075670 | Team from Source to Tyne | ROWLETCH BURN |  |  | Commissioned pre-2016 - full year data expected | 0.75 | 2 | 99.96%
Northumbrian Water | KINGSWAY/PRINCESS STREET CSO | 6NW801116 | 235/1873 | 235/1873 |  | SO on sewer network | NZ2089058860 | GB103023075670 | Team from Source to Tyne | BLACK BURN |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | KIRK STREET CSO | 6NW801486 | 254/1834 | 254/1834 |  | SO on sewer network | NZ3727023220 | GB103025072360 | Billingham Beck from Bishopton Bck to Brierle | CULVERTED W/C TO BISHOPTON BEC |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 93.3%
Northumbrian Water | KIRKBY SEWAGE PUMPING STATION CSO | 6NW800667 | 25/04/1636 | 25/04/1636 | 25/04/1636-03 | Storm discharge at pumping station | NZ5362005880 | GB103025071890 | Leven from Source to Tame | THE WEST BECK - LEVEN |  |  | Commissioned in 2017 - full year data expected | 0 | 0 | 88.05% | Comms failure / issue | Resolved - April
Northumbrian Water | KIRKLEVINGTON SEWAGE TREATMENT WORK | 6NW800791 | 25/04/1773 | 25/04/1773 | 25/04/1773-02 | Storm tank at WwTW | NZ4272010310 | GB103025072050 | Saltergill Beck Catchment (trib of Tees) | SALTERGILL BECK, TEES CATCHMET |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | KLONDYKE CSO | 6NW801291 | 226/1182 | 226/1182 |  | SO on sewer network | NZ2755276116 | GB103022076190 | Seaton Burn from Source to Tidal Limit | SEATON BURN |  |  | Commissioned pre-2016 - full year data expected | 136.5 | 40 | 99.77%
Northumbrian Water | KNITSLEY SEWAGE TREATMENT WORKS | 6NW800805 | 244/1028 | 244/1028 | A2 | Storm tank at WwTW | NZ1244748118 | GB103024077330 | Smallhope Burn from Source to Browney, Stocke | Smallhope Burn |  |  | Commissioned in 2020 - full year data expected | 458.1953 | 42 | 65.12% | Comms failure / issue | N/A - Ongoing investigation
Northumbrian Water | KYLOE VIEW SSO | 6NW800211 | 210/0995 | 210/0995 |  | SO on sewer network | NU0218339803 | GB103021073221 | South Low from Source to Haggerston Bridge | TRIBUTARY OF THE LOW |  |  | Commissioned in 2016 - full year data expected | 63.75 | 23 | 99.6%
Northumbrian Water | ANDREWS HOUSE LA HACIENDA CSO | 6NW800952 | 233/1265 | 233/1265 |  | SO on sewer network | NZ0928763520 | GB103023075801 | Tyne from Watersmeet to Tidal Limit | TYNE (UNAMED TRIB.) |  |  | Commissioned pre-2016 - full year data expected | 73.9667 | 21 | 96.11%
Northumbrian Water | GREYSTONE RD SSO SOUTH LACKENBY | 6NW801598 | 256/E/0259 | 256/E/0259 |  | SO on sewer network | NZ5647019710 | GB103025072320 | Tees Estuary (S Bank) | KETTLE BECK |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | LAKES CSO | 6NW800437 | 256/1066 | 256/1066 |  | SO on sewer network | NZ5983025520 | GB650301500005 | Tees Coastal | NORTH SEA |  | Redcar Coatham | Commissioned in 2019 - full year data expected | 1117.5419 | 122 | 99.93%
Northumbrian Water | LAMESLEY SSO | 6NW801208 | 235/D/0266 | 235/D/0266 |  | SO on sewer network | NZ2520057800 | GB103023075670 | Team from Source to Tyne | TEAM |  |  | Commissioned pre-2016 - full year data expected | 283.5 | 33 | 95.79%
Northumbrian Water | LADY PARK PUMPING STATION LAMESLEY | 6NW800452 | 235/A/0837 | 235/A/0837 |  | Storm discharge at pumping station | NZ2490058600 | GB103023075670 | Team from Source to Tyne | TEAM |  |  | Mar 2021 | 0 | 0 | 99.99%
Northumbrian Water | LAMPORT CSO | 6NW801373 | 235/1051 | 235/1051 |  | SO on sewer network | NZ3026065370 | GB510302310200 | TYNE | TYNE (TIDAL) |  |  | Commissioned pre-2016 - full year data expected | 6.5 | 9 | 97.8%
Northumbrian Water | LANCHESTER AVENUE CSO | 6NW801286 | 235/1956 | 235/1956 |  | SO on sewer network | NZ2871059350 | GB103023075690 | Don from Source to Tidal Limit | RIVER DON |  |  | Commissioned pre-2016 - full year data expected | 3.5 | 5 | 99.99%
Northumbrian Water | LANCHESTER STW | 6NW800737 | 244/0986 | 244/0986 | 244/0986-03 | Storm tank at WwTW | NZ1735046570 | GB103024077330 | Smallhope Burn from Source to Browney, Stocke | SMALLHOPE BURN |  |  | Commissioned in 2020 - full year data expected | 1191.2758 | 83 | 100%
Northumbrian Water | COCKFIELD P.S. & LANDS FARM CSO | 6NW800991 | 242/1028 | 242/1028 |  | SO on sewer network | NZ1362324909 | GB103024072690 | Gaunless from Source to Hummer Beck | River Gaunless |  |  | Commissioned pre-2016 - full year data expected | 40.75 | 14 | 99.63%
Northumbrian Water | LANEHEAD PUMPING STATION | 6NW800462 | 223/0840 | 223/0840 | A | Storm discharge at pumping station | NU1733002340 | GB103022076693 | Coquet from Forest Burn to Tidal Limit | EAST HOUSE BURN |  |  | Commissioned in 2020 - full year data expected | 687.1158 | 61 | 99.27%
Northumbrian Water | LANEHEAD STW | 6NW800129 | 231/0922 | 231/0922 | A2 | Inlet SO at WwTW | NY7880085880 | GB103023074991 | Tarset Burn from Black Burn to N Tyne | TARSET BURN |  |  | May 2021 | #N/A | #N/A | 0% | Sensor failure / issue | N/A - Ongoing investigation
Northumbrian Water | LANGLEY BECK CSO | 6NW801487 | 25/03/1251 | 25/03/1251 |  | SO on sewer network | NZ3780735531 | GB103025076070 | Skerne from Source to Carrs | LANGLEY BECK |  |  | Commissioned pre-2016 - full year data expected | 86.75 | 39 | 84.99% | Comms failure / issue | Resolved - March | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution
Northumbrian Water | LANGTON BECK PS | 6NW800512 | 252/1001 | 252/1001 | 252/1001-A (Storm Sewage) | Storm discharge at pumping station | NZ1746019760 | GB103025072300 | Piercebridge Beck from Source to Tees | LANGTON BECK (TEES) |  |  | Commissioned in 2019 - full year data expected | 422.7753 | 76 | 100%
Northumbrian Water | LANSBURY DRIVE CSO | 6NW801238 | 235/1885 | 235/1885 |  | SO on sewer network | NZ2612056580 | GB103023075670 | Team from Source to Tyne | RIVER TEAM |  |  | Commissioned pre-2016 - full year data expected | 62 | 27 | 95.58%
Northumbrian Water | LANYTYS LONNEN CSO | 6NW800875 | 232/0999 | 232/0999 |  | SO on sewer network | NY7097863640 | GB103023075532 | South Tyne from Tipalt Burn to Allen | RIVER SOUTH TYNE |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 97.13%
Northumbrian Water | LAUREL AVENUE CSO | 6NW801309 | 245/1261 | 245/1261 |  | SO on sewer network | NZ2893042510 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | PELAW WOOD BECK (RIVER WEAR) |  |  | Commissioned pre-2016 - full year data expected | 55.75 | 37 | 99.24%
Northumbrian Water | LAYLAND BRIDGE CSO | 6NW801620 | 256/1072 | 256/1072 |  | SO on sewer network | NZ6690918554 | GB103025071960 | Saltburn Gill Catch trib of North Sea | WHITE CROSS BECK |  | Saltburn Pier | Commissioned pre-2016 - full year data expected | 0.26667 | 2 | 99.79%
Northumbrian Water | LAYLAND BRIDGE PUMPING STATION | 6NW800671 | 256/1073 | 256/1073 | 256/1073-01 | Storm discharge at pumping station | NZ6714018940 | GB103025071960 | Saltburn Gill Catch trib of North Sea | WHITE CROSS BECK |  | Saltburn Pier | Commissioned in 2018 - full year data expected | 104.1011 | 31 | 100%
Northumbrian Water | LEALHOME GROVE CSO | 6NW801519 | 254/1931 | 254/1931 |  | SO on sewer network | NZ4179518687 | GB103025072550 | Lustrum Beck Catchment (trib of Tees) | HARTBURN BECK TRIBUTARY |  |  | Commissioned pre-2016 - full year data expected | 1.5 | 5 | 99.99%
Northumbrian Water | LEAMSIDE CSO | 6NW801364 | 245/1295 | 245/1295 |  | SO on sewer network | NZ2990046700 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | WEAR |  |  | Commissioned pre-2016 - full year data expected | 70.5 | 17 | 99.99%
Northumbrian Water | WEST RAINTON STW LEAMSIDE | 6NW800772 | 245/1271 | 245/1271 | 245/1271-03 | Storm tank at WwTW | NZ2970046640 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | WEAR |  |  | Commissioned in 2020 - full year data expected | 56.3064 | 11 | 78.76% | Installation set-up/design issue | Resolved - March
Northumbrian Water | LEASINGTHORPE FARM CSO | 6NW801194 | 25/03/1252 | 25/03/1252 |  | SO on sewer network | NZ2582930168 | GB103025072450 | Rushyford Beck from Source to Woodham Burn | RUSHYFORD BECK |  |  | Commissioned pre-2016 - full year data expected | 74.25 | 57 | 76.31% | Comms failure / issue | Resolved - July
Northumbrian Water | LEASINGTHORNE SPS CSO | 6NW801193 | 25/03/1268 | 25/03/1268 | A1 | Storm discharge at pumping station | NZ2572230191 | GB103025072450 | Rushyford Beck from Source to Woodham Burn | RUSHYFORD BECK |  |  | Commissioned pre-2016 - full year data expected | 186 | 62 | 99.39%
Northumbrian Water | LESBURY(HIPSBURN)CSO | 6NW800865 | 222/G/0185 | 222/G/0185 |  | SO on sewer network | NU2365010930 | 6 | #N/A | HIPS BURN |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 90.67%
Northumbrian Water | LEVENSIDE/MANOR CLOSE CSO | 6NW801589 | QR.25/04/1571 | QR.25/04/1571 |  | SO on sewer network | NZ5267008555 | GB103025071890 | Leven from Source to Tame | RIVER LEVEN |  |  | Commissioned pre-2016 - full year data expected | 188 | 31 | 99.88%
Northumbrian Water | LIME STREET/CUT BANK (2) | 6NW801246 | 235/1957 | 235/1957 |  | SO on sewer network | NZ2633564341 | GB510302310200 | TYNE | OUSE BURN ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 210.7936 | 52 | 99.92% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | LIMEKILN GILL SAMPLING PT. FOR EA18 | 6NW800644 | 255/1114 | 255/1114 | A | Storm discharge at pumping station | NZ4772038310 | GB650301500002 | Tyne and Wear | NORTH SEA |  |  | Commissioned in 2020 - full year data expected | 73.6172 | 9 | 98.25%
Northumbrian Water | LINDOM AVENUE CSO | 6NW800333 | 245/1379 | 245/1379 |  | SO on sewer network | NZ2799951355 | GB103024077624 | Wear DS of Lumley Park Burn to Tidal Limit | RIVER WEAR |  |  | Commissioned in 2018 - full year data expected | 259.9647 | 35 | 100%
Northumbrian Water | BLYTH NO 2 PS LINKS ROAD | 6NW800364 | 226/1075 | 226/1075 |  | SO on sewer network | NZ3217080090 | GB650301500002 | Tyne and Wear | NORTH SEA |  | Blyth South Beach | EDM to be installed by December 2023 | #N/A | #N/A | #N/A
Northumbrian Water | LINKS ROAD CSO | 6NW801441 | #TBC | Permit Anomaly | To be permitted for storm | SO on sewer network | NZ3361076757 | GB650301500002 | Tyne and Wear | Seaton Burn |  | Seaton Sluice | Commissioned pre-2016 - full year data expected | 0.63333 | 8 | 89.8% | Comms failure / issue | Scheduled
Northumbrian Water | LINTON PS | 6NW800540 | 224/0958 | 224/0958 | 224/0958-02 | Storm discharge at pumping station | NZ2644091130 | GB103022076820 | Lyne from Source to Tidal Limit | POTLAND BURN |  |  | Commissioned in 2020 - full year data expected | 22.025 | 5 | 100%
Northumbrian Water | LINTZ TERRACE CSO | 6NW801064 | 235/1708 | 235/1708 |  | SO on sewer network | NZ1818052630 | GB103023075670 | Team from Source to Tyne | TRIB KYO BURN |  |  | Commissioned pre-2016 - full year data expected | 5.25 | 9 | 99.78%
Northumbrian Water | LIVERTON MINES SSO | 6NW800674 | 256/C/0407 | 256/C/0407 | 256/C/0407-A1 | Storm discharge at pumping station | NZ7140818205 | GB103025071940 | Middle Gill Beck from Source to Kilton Beck | WHITE CLIFFE BECK |  |  | Commissioned pre-2016 - full year data expected | 56.25 | 11 | 99.96%
Northumbrian Water | LOCAL AVENUE | 6NW801420 | 245/1203 | 245/1203 |  | SO on sewer network | NZ3321042420 | GB103024077540 | Pittington Beck from Coalford to Old Durham Beck | COLDWELL BURN |  |  | Commissioned pre-2016 - full year data expected | 29.25 | 29 | 99.43%
Northumbrian Water | LOCKE PARK CSO | 6NW800436 | 254/1911 | 254/1911 |  | SO on sewer network | NZ5923024820 | GB103025072320 | Tees Estuary (S Bank) | THE FLEET |  |  | Commissioned in 2016 - full year data expected | 7 | 3 | 97.01%
Northumbrian Water | BRIARDENE LOCKHAUGH ROAD CSO | 6NW801055 | 234/A/1025 | 234/A/1025 |  | SO on sewer network | NZ1700059500 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | DERWENT, TRIBUTARY OF |  |  | Commissioned pre-2016 - full year data expected | 9.5 | 8 | 98.73%
Northumbrian Water | LOCKHAUGH STW | 6NW800157 | 234/1072 | 234/1072 | A3 | Inlet SO at WwTW | NZ1740058900 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | RIVER DERWENT |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | LOCKHAUGH STW | 6NW800738 | 234/1072 | 234/1072 | A2 | Storm tank at WwTW | NZ1740058900 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | RIVER DERWENT |  |  | Commissioned in 2020 - full year data expected | 863.8264 | 73 | 100%
Northumbrian Water | LONDONDERRY ROAD/GREEN LANE CSO | 6NW800625 | #TBC | Permit Anomaly | To be permitted for storm | SO on sewer network | NZ4377519746 | GB103025072550 | Lustrum Beck Catchment (trib of Tees) | Lustrum Beck |  |  | Commissioned pre-2016 - full year data expected | 6.75 | 7 | 50.72% | Comms failure / issue | Scheduled
Northumbrian Water | LONG BRIDGE CSO | 6NW801154 | QC.25/02/1070 | QC.25/02/1070 |  | SO on sewer network | NZ2314309135 | GB103025072040 | Barton Beck from Source to Clow Beck | BARTON BECK |  |  | Commissioned pre-2016 - full year data expected | 61.25 | 10 | 77.3% | Comms failure / issue | Resolved - September
Northumbrian Water | NEW MARSKE METHODIST CHURCH LONGBECK | 6NW801613 | 25/06/1018 | 25/06/1018 |  | SO on sewer network | NZ6296422768 | GB650301500005 | Tees Coastal | NORTH SEA |  | Marske | Commissioned pre-2016 - full year data expected | 20.3333 | 17 | 99.83%
Northumbrian Water | LONGBYRE STW | 6NW800124 | 232/1155 | 232/1155 | 232/1155-03 | Inlet SO at WwTW | NY6564066240 | GB103023075580 | Tipalt Burn from Source to South Tyne | POW CHARNEY BURN |  |  | Commissioned in 2020 - full year data expected | 14.7419 | 5 | 91.51%
Northumbrian Water | LONGHIRST STW | 6NW800751 | 225/A/0861 | 225/A/0861 |  | Storm tank at WwTW | NZ2254088750 | GB103022077030 | Bothal Burn Catchment (trib of Wansbeck) | LONGHIRST BURN |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | LONGHORSLEY STW | 6NW800733 | 223/0633 | 223/0633 | A2 | Storm tank at WwTW | NZ1551694375 | GB103022076550 | Longdike Burn Catchment (trib of Coquet) | PAXTONDEAN BURN |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | LONGNEWTON CSO STO07 | 6NW801492 | NPSWQD009184 | NPSWQD009184 |  | SO on sewer network | NZ3896216643 | GB103025072550 | Lustrum Beck Catchment (trib of Tees) | LONGNEWTON BECK |  |  | Commissioned pre-2016 - full year data expected | 91.25 | 37 | 78.09% | Sensor failure / issue | Resolved - October
Northumbrian Water | LONG NEWTON SEWAGE TREATMENT WORKS | 6NW800789 | 254/1940 | 254/1940 | 254/1940-02 | Storm tank at WwTW | NZ3898016640 | GB103025072550 | Lustrum Beck Catchment (trib of Tees) | LONGNEWTON BECK-(TEES CATCHMNT |  |  | Commissioned in 2020 - full year data expected | 396.7481 | 37 | 100%
Northumbrian Water | LOVE AVENUE COTTAGES CSO (NTY 009) | 6NW801253 | 226/1258 | 226/1258 |  | SO on sewer network | NZ2657973533 | GB103022076190 | Seaton Burn from Source to Tidal Limit | SEATON BURN |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | LOW FELL CSO | 6NW801183 | 235/1961 | 235/1961 |  | SO on sewer network | NZ2500060500 | GB103023075670 | Team from Source to Tyne | TEAM, TRIBUTARY OF |  |  | Commissioned in 2020 - full year data expected | 0 | 0 | 93.32%
Northumbrian Water | LOW HAUXLEY PS | 6NW800483 | 224/0961 | 224/0961 | 224/0961-02 | Storm discharge at pumping station | NU2862002820 | GB650301500001 | Northumberland South | NORTH SEA |  |  | Commissioned in 2020 - full year data expected | 15.4778 | 8 | 99.76%
Northumbrian Water | LOW HEWORTH LANE PUMPING STATION | 6NW801316 | 235/1750 | 235/1750 | 235/1750-01 | SO on sewer network | NZ2868062710 | GB510302310200 | TYNE | RIVER TYNE SALINE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 178 | 35 | 99.93%
Northumbrian Water | WITTON-LE-WEAR PS LOW LANE | 6NW801005 | 241/1080 | 241/1080 | 241/1080-01 | Storm discharge at pumping station | NZ1537031340 | GB103024077462 | Wear from Houselop Beck to Beechburn Beck | RIVER WEAR |  |  | Commissioned pre-2016 - full year data expected | 890.75 | 77 | 88.66% | Comms failure / issue | Scheduled | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | LOW PITTINGTON PUMPING STATION | 6NW801404 | 245/1288 | 245/1288 | 245/1288-01 | Storm discharge at pumping station | NZ3248044731 | GB103024077540 | Pittington Beck from Coalford to Old Durham Beck | PITTINGTON BECK |  |  | Commissioned pre-2016 - full year data expected | 1200.25 | 62 | 99.85%
Northumbrian Water | LOW SOUTHWICK PUMPING STATION | 6NW800608 | 245/1209 | 245/1209 | 245/1209-01 | Storm discharge at pumping station | NZ3837057910 | GB510302402900 | WEAR | RIVER WEAR (SALINE ESTUARY) |  |  | Commissioned pre-2016 - full year data expected | 195.5 | 62 | 99.86% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | LOW WADSWORTH PS | 6NW801043 | 241/1081 | 241/1081 | 241/1081-01 | Storm discharge at pumping station | NZ1760030870 | GB103024077462 | Wear from Houselop Beck to Beechburn Beck | RIVER WEAR |  |  | Commissioned pre-2016 - full year data expected | 860 | 59 | 94.41% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | LOW WADSWORTH STW | 6NW800736 | 241/1097 | 241/1097 | 241/1097-03 | Storm tank at WwTW | NZ1812030820 | GB103024077462 | Wear from Houselop Beck to Beechburn Beck | WEAR |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | LOW WILLINGTON PARK CSO | 6NW801108 | 243/0983 | 243/0983 |  | SO on sewer network | NZ2043734545 | GB103024077464 | Wear from Gaunless to Browney | RIVER WEAR |  |  | Commissioned pre-2016 - full year data expected | 134.5 | 42 | 99.87%
Northumbrian Water | LOWICK SEWAGE TREATMENT WORKS CSO INLET | 6NW800110 | 210/A/0854 | 210/A/0854 | A3 | Inlet SO at WwTW | NU0257239688 | GB103021073221 | South Low from Source to Haggerston Bridge | TRIBUTARY OF THE LOW |  |  | Commissioned in 2020 - full year data expected | 2.5144 | 13 | 60.46% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | LOWICK SEWAGE TREATMENT WORKS Storm Tank | 6NW800809 | 210/A/0854 | 210/A/0854 | A2 | Storm tank at WwTW | NU0257239688 | GB103021073221 | South Low from Source to Haggerston Bridge | TRIBUTARY OF THE LOW |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | LUMLEY SEWAGE PUMPING STATION | 6NW800553 | 245/1055 | Permit Anomaly - EO permit 245/1055 | To be permitted for storm | Storm discharge at pumping station | NZ2843550888 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | River Wear |  |  | Commissioned in 2020 - full year data expected | 8.9697 | 3 | 99.99%
Northumbrian Water | LUSTRUM HIGH LEVEL CSO | 6NW801531 | 254/1830 | 254/1830 |  | SO on sewer network | NZ4305018748 | GB103025072550 | Lustrum Beck Catchment (trib of Tees) | LUSTRUM BECK |  |  | Commissioned pre-2016 - full year data expected | 129.25 | 49 | 99.01%
Northumbrian Water | LYNDHURST ROAD COMBINED SEWER OVERF | 6NW801335 | 253/1090 | 253/1090 |  | SO on sewer network | NZ2902029130 | GB103025072450 | Rushyford Beck from Source to Woodham Burn | RUSHYFORD BECK TRIBUTARY |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.03%
Northumbrian Water | LYNDHURST ROAD CSO | 6NW801324 | NPSWQD005300 | NPSWQD005300 |  | SO on sewer network | NZ2892985584 | GB103025072450 | Rushyford Beck from Source to Woodham Burn | RIVER WANSBECK |  | Newbiggin North & Newbiggin South | Commissioned pre-2016 - full year data expected | 23.3667 | 22 | 93.96%
Northumbrian Water | LYNE CSO CM045 | 6NW801325 | 224/0999 | 224/0999 |  | SO on sewer network | NZ2866791593 | 362 | #N/A | LYNE |  |  | Commissioned pre-2016 - full year data expected | 350.75 | 64 | 97.59% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | LYNEMOUTH STW | 6NW800774 | 224/0993 | 224/0993 | 224/0993-04 | Storm tank at WwTW | NZ3010090890 | GB650301500001 | Northumberland South | R LYNE (SALINE ESTUARY) |  |  | Commissioned in 2020 - full year data expected | 2238.1317 | 126 | 100%
Northumbrian Water | LYNESACK AND SOFTLEY CSO (TE 011) | 6NW800234 | 242/1065 | 242/1065 |  | SO on sewer network | NZ1111625534 | GB103024072690 | Gaunless from Source to Hummer Beck | CROW HOWLE BECK |  |  | Commissioned in 2017 - full year data expected | 0 | 0 | 30.26% | Access - Unable to retrieve data from non-telemetry data logger (NB: not to be used for delayed access to fix existing fault) | Scheduled
Northumbrian Water | LYNWOOD HOUSE CSO DER44 | 6NW801025 | 244/1021 | 244/1021 |  | SO on sewer network | NZ1678047071 | GB103024077330 | Smallhope Burn from Source to Browney, Stocke | SMALLHOPE BURN |  |  | Commissioned pre-2016 - full year data expected | 281 | 71 | 97.85% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | LYSNDON FARM CSO | 6NW801399 | 226/1196 | 226/1196 |  | SO on sewer network | NZ3101477666 | 363 | #N/A | LYSDON BURN (COASTAL STREAM) |  | Blyth South Beach | Commissioned pre-2016 - full year data expected | 357.9 | 35 | 97.29%
Northumbrian Water | MAFEKING COMBINED SEWER OVERFLOW | 6NW801125 | EPRAB3196VY | EPRAB3196VY |  | SO on sewer network | NZ2018585520 | GB103022077061 | Wansbeck from Font to Bothal Burn | CHURCH BURN |  |  | Commissioned pre-2016 - full year data expected | 1.75 | 3 | 99.99%
Northumbrian Water | MAGDALEN FIELDS SOUTH COMBINED SEWW | 6NW800840 | 210/1362 | 210/1362 |  | SO on sewer network | NU0010954736 | GB650301440000 | Northumberland North | NORTH SEA |  |  | Commissioned pre-2016 - full year data expected | 315 | 58 | 58.34% | Comms failure / issue | Resolved - November | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | MAGDALENE FIELDS NORTH CSO High level M3 monitoring point | 6NW800837M3 | 210/1355 | 210/1355 | A1 | SO on sewer network | NU0009954653 | GB650301440000 | Northumberland North | NORTH SEA |  |  | Commissioned pre-2016 - full year data expected | 0.25 | 1 | 99.99%
Northumbrian Water | MAGDALENE FIELDS NORTH CSO M2 monitoring point | 6NW800837M2 | 210/1355 | 210/1355 | A1 | SO on sewer network | NU0009954653 | GB650301440000 | Northumberland North | NORTH SEA |  |  | Commissioned pre-2016 - full year data expected | 251.5 | 79 | 88.7% | Sensor failure / issue | Resolved - August | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | MAIN STREET CSO | 6NW800852 | 223/0951 | 223/0951 |  | SO on sewer network | NU1854300330 | GB103022076693 | Coquet from Forest Burn to Tidal Limit | RIVER COQUET |  |  | Commissioned pre-2016 - full year data expected | 4.25 | 7 | 77.45% | Comms failure / issue | Resolved - March
Northumbrian Water | CSO MAIN STREET | 6NW800814 | 210/1284 | 210/1284 |  | SO on sewer network | NT8971038130 | GB103022076693 | Coquet from Forest Burn to Tidal Limit | THE PALLIN'S BURN |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 91.66%
Northumbrian Water | MAIN STREET CSO | 6NW800813 | 210/1291 | 210/1291 |  | SO on sewer network | NT8569039070 | GB103022076693 | Coquet from Forest Burn to Tidal Limit | DUDDO BURN, TRIBUTARY OF |  |  | Commissioned pre-2016 - full year data expected | 57 | 33 | 99.89%
Northumbrian Water | MAIN STREET CSO | 6NW800876 | 232/1012 | 232/1012 |  | SO on sewer network | NY7092064110 | GB103022076693 | Coquet from Forest Burn to Tidal Limit | HEMMEL BURN |  |  | Commissioned pre-2016 - full year data expected | 1 | 4 | 99.3%
Northumbrian Water | MAIN STREET SPITTAL CSO | 6NW800843 | 210/1349 | 210/1349 |  | SO on sewer network | NU0018151930 | GB510202110000 | TWEED | NORTH SEA |  | Spittal | Commissioned pre-2016 - full year data expected | 0.6 | 2 | 100%
Northumbrian Water | MAINSFORTH TERRACE CSO SU63 | 6NW800407 | 255/1208 | 255/1208 |  | SO on sewer network | NZ4108456147 | GB650301500002 | Tyne and Wear | NORTH SEA |  |  | Commissioned in 2017 - full year data expected | 0 | 0 | 37.06% | Comms failure / issue | Scheduled
Northumbrian Water | MAINSFORTH TERRACE PS | 6NW800658 | 255/1095 | 255/1095 | 255/1095-3B | Storm discharge at pumping station | NZ5182031900 | GB650301500005 | Tees Coastal | NORTH SEA |  | Seaton Carew (North) | Commissioned in 2018 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | MAINSFORTH TERRACE PS | 6NW800659 | 255/1095 | 255/1095 | 255/1095-3A | Storm discharge at pumping station | NZ5182031900 | GB650301500005 | Tees Coastal | NORTH SEA |  | Seaton Carew (North) | EDM to be installed by December 2023 | #N/A | #N/A | #N/A
Northumbrian Water | MANFIELD SEWAGE DISPOSAL WORKS SSO CSO INLET | 6NW801142(2) | 252/E/0279 | 252/E/0279 | B | Inlet SO at WwTW | NZ2250013600 | GB103025072190 | Tees from River Greta to River Skerne | TEES, DITCH TO |  |  | EDM to be installed by December 2023 | #N/A | #N/A | #N/A
Northumbrian Water | MANFIELD SEWAGE DISPOSAL WORKS Network CSO INLET | 6NW801142(1) | 252/E/0279 | 252/E/0279 | A | SO on sewer network | NZ2250013600 | GB103025072190 | Tees from River Greta to River Skerne | TEES, DITCH TO |  |  | Commissioned pre-2016 - full year data expected | 301.5 | 55 | 95.12% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution
Northumbrian Water | CSO MANOR COURT | 6NW800249 | 244/0940 | 244/0940 |  | SO on sewer network | NZ1701646861 | GB103024077330 | Smallhope Burn from Source to Browney, Stocke | SMALLHOPE BURN |  |  | Commissioned in 2017 - full year data expected | 535.5 | 83 | 99.98% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | MANOR GARDENS CSO | 6NW801370 | 235/1965 | 235/1965 |  | SO on sewer network | NZ2966362978 | GB510302310200 | TYNE | RIVER TYNE (ESTUARY) |  |  | Commissioned pre-2016 - full year data expected | 73 | 15 | 98.22%
Northumbrian Water | MARINE DRIVE PUMPING STATION | 6NW800585 | 235/1389 | 235/1389 | 235/1389-01 | Storm discharge at pumping station | NZ3233963223 | GB103023075690 | Don from Source to Tidal Limit | MONKTON BURN, TRIB OF R. DON |  |  | Commissioned in 2020 - full year data expected | 1.5931 | 2 | 100%
Northumbrian Water | SALTBURN ATTENUATION TANK NO2 MARINE PARADE | 6NW800444 | 25/06/0984 | 25/06/0984 |  | SO on sewer network | NZ6609021770 | GB650301500005 | Tees Coastal | PIT HILLS STELL NORTH SEA |  | Saltburn Pier | Commissioned in 2019 - full year data expected | 0.0036111 | 1 | 99.65%
Northumbrian Water | MARKET LANE CSO | 6NW800267 | 234/0934 | 234/0934 |  | SO on sewer network | NZ2042062947 | 8 | #N/A | RIVER DERWENT |  |  | Commissioned in 2019 - full year data expected | 593 | 65 | 100%
Northumbrian Water | MARKET LANE CSO | 6NW801141 | 234/1017 | 234/1017 |  | SO on sewer network | NZ2145361776 | 8 | #N/A | TYNE TRIB |  |  | Commissioned pre-2016 - full year data expected | 414.5 | 65 | 98.32% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | MARSKE SEWAGE TREATMENT WORKS | 6NW800203(2) | 25/06/1015 | 25/06/1015 | 25/06/1015-05 | Inlet SO at WwTW | NZ6405024200 | GB650301500005 | Tees Coastal | NORTH SEA |  | Marske | Commissioned in 2020 - full year data expected | 634.2078 | 96 | 100%
Northumbrian Water | CSO 1 MARTON AVENUE | 6NW801582(1) | 25/04/1600 | 25/04/1600 | 25/04/1600-1 | SO on sewer network | NZ5174017150 | GB103025072210 | Marton West Beck Catchment (trib of Tidal Tees) | ORMESBY BECK |  |  | Commissioned pre-2016 - full year data expected | 0.25 | 1 | 99.43%
Northumbrian Water | CSO 1 MARTON AVENUE | 6NW801582(2) | 25/04/1600 | 25/04/1600 | 25/04/1600-2 | SO on sewer network | NZ5174017150 | GB103025072210 | Marton West Beck Catchment (trib of Tidal Tees) | ORMESBY BECK |  |  | Commissioned pre-2016 - full year data expected | 20.25 | 11 | 99.98%
Northumbrian Water | MARY MAGDALENE NO3 CSO (TD037) | 6NW800953 | 233/1250 | 233/1250 |  | SO on sewer network | NZ0927463327 | GB103023075801 | Tyne from Watersmeet to Tidal Limit | UNNAMED TRIB OF RIVER TYNE |  |  | Commissioned pre-2016 - full year data expected | 235.8333 | 45 | 83.3% | Sensor failure / issue | Resolved - December
Northumbrian Water | MAUGHAN CLOSE CSO SE39 | 6NW801359 | 243/1001 | 243/1001 |  | SO on sewer network | NZ3084034670 | GB103024077410 | Croxdale Beck from Source to Wear | COXHOE BECK TRIB |  |  | Commissioned pre-2016 - full year data expected | 9.75 | 11 | 99.85%
Northumbrian Water | MAYFAIR ROAD CSO | 6NW801333 | 253/1274 | 253/1274 |  | SO on sewer network | NZ2956017800 | GB103025072596 | Skerne from Demons Beck to Tees | RIVER TEES |  |  | Commissioned pre-2016 - full year data expected | 0.5 | 2 | 97.57%
Northumbrian Water | MAYFIELD AVE CSO NC034 | 6NW801033 | 233/1268 | 233/1268 |  | SO on sewer network | NZ1635666370 | GB103023075740 | New Burn (Trib of Tyne) | NEW BURN |  |  | Commissioned pre-2016 - full year data expected | 50.1 | 26 | 100%
Northumbrian Water | MAYFIELD CSO | 6NW801195 | 243/0972 | 243/0972 |  | SO on sewer network | NZ2559034620 | GB103024077350 | Valley Burn from Source to Wear | VALLEY BURN |  |  | Commissioned pre-2016 - full year data expected | 250 | 57 | 99.63% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution
Northumbrian Water | MCCLEAN AVENUE CSO (REF NO L15) | 6NW801603 | 254/1915 | 254/1915 |  | SO on sewer network | NZ5867024240 | GB103025072320 | Tees Estuary (S Bank) | FLEET BECK (TRIB) |  |  | Commissioned pre-2016 - full year data expected | 118.25 | 32 | 99.44%
Northumbrian Water | MEADOW VIEW CSO | 6NW800873 | NPSWQD003443 | NPSWQD003443 |  | SO on sewer network | NY6861461700 | GB103023075500 | Park Burn from Source to South Tyne | PARK BURN |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 56.68% | Comms failure / issue | N/A - Ongoing investigation
Northumbrian Water | MELKRIDGE STW | 6NW800128 | 232/1156 | 232/1156 | 232/1156-03 | Inlet SO at WwTW | NY7435063780 | GB103023075532 | South Tyne from Tipalt Burn to Allen | RIVER SOUTH TYNE |  |  | Commissioned in 2020 - full year data expected | 85.3286 | 63 | 99.98%
Northumbrian Water | MELSONBY SEWAGE TREATMENT WORKS | 6NW800741 | 25/02/1108 | 25/02/1108 | A2 | Storm tank at WwTW | NZ2050008300 | GB103025072040 | Barton Beck from Source to Clow Beck | WATERFALL BECK (CLOW BECK CATC |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | MEMORIAL HALL SSO | 6NW801035 | 226/0100 | 226/0100 |  | SO on sewer network | NZ1638772732 | GB103022076860 | Pont from Med Burn to Small Burn | PONT |  |  | Commissioned pre-2016 - full year data expected | 465.5 | 65 | 99.7% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | MERRYSHIELDS CSO | 6NW800932 | 233/1255 | 233/1255 |  | SO on sewer network | NZ0599061540 | GB103023075801 | Tyne from Watersmeet to Tidal Limit | BELLASSIS BURN |  |  | Commissioned pre-2016 - full year data expected | 75.5 | 31 | 99.41%
Northumbrian Water | METAL BRIDGE SPS AND CSO | 6NW800569 | 243/1011 | 243/1011 | A1 | Storm discharge at pumping station | NZ3007835028 | GB103024077410 | Croxdale Beck from Source to Wear | EAST HOWLE BECK |  |  | Commissioned in 2019 - full year data expected | 18.4592 | 9 | 100%
Northumbrian Water | METROCENTRE GREEN CAR PARK PS (E7) | 6NW800279 | 235/2002 | 235/2002 |  | SO on sewer network | NZ2225062910 | GB510302310200 | TYNE | TYNE (SLAINE ESTUARY) |  |  | Commissioned in 2020 - full year data expected | 229.1208 | 129 | 99.8% |  |  | Performance - Infiltration
Northumbrian Water | MICKLETON SEWAGE TREATMENT WORKS | 6NW800709 | 251/0940 | 251/0940 | 251/0940-03 | Storm tank at WwTW | NY9740023910 | GB103025072511 | Tees from Maize Beck to Percy Beck | HEUGH SYKE - TRIB. OF R. TEES |  |  | Commissioned in 2020 - full year data expected | 308.1217 | 59 | 99.43%
Northumbrian Water | LEVEN ROAD CSO | 6NW000007 | 254/1895 | 254/1895 |  | SO on sewer network | NZ5141020030 | 10 | #N/A | ORMESBY BECK |  |  | Commissioned pre-2016 - full year data expected | 86.25 | 36 | 99.99%
Northumbrian Water | CSO AND SPS AT MIDDLESBROUGH ROAD | 6NW800637 | QC.25/04/1585 | QC.25/04/1585 | QC.25/04/1585-S1 Storm Sewage | Storm discharge at pumping station | NZ4616019040 | GB103025072595 | Tees from Skerne to Tidal Limit | THE RIVER TEES SALINE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 6.5 | 6 | 99.68%
Northumbrian Water | MIDDLETON AIRPORT STORM TW | 6NW800784 | EPRPB3193VX | EPRPB3193VX | A1 | Storm discharge at pumping station | NZ3539911878 | GB103025072595 | Tees from Skerne to Tidal Limit | RIVER TEES |  |  | Commissioned in 2018 - full year data expected | 1555.2389 | 81 | 100% |  |  | Performance - Infiltration
Northumbrian Water | MIDDLETON ONE ROW CSO | 6NW801457 | 254/1540 | QR.25/04/1540 |  | SO on sewer network | NZ3501812262 | GB103025072595 | Tees from Skerne to Tidal Limit | THE RIVER TEES |  |  | Commissioned pre-2016 - full year data expected | 311.75 | 51 | 99.27% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | MIDDLETON-IN-TEESDALE SEWAGE TREATM CSO INLET | 6NW800901 | 25/01/0919 | 25/01/0919 | 25/01/0919-03 | Inlet SO at WwTW | NY9526024910 | GB103025072511 | Tees from Maize Beck to Percy Beck | RIVER TEES |  |  | Commissioned pre-2016 - full year data expected | 17.25 | 23 | 99.45%
Northumbrian Water | MIDDLETON-IN-TEESDALE SEWAGE TREATM Storm Tank | 6NW800707 | 25/01/0919 | 25/01/0919 | 25/01/0919-02 | Storm tank at WwTW | NY9526024910 | GB103025072511 | Tees from Maize Beck to Percy Beck | RIVER TEES |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | MID-TYNE NO,3 CSO | 6NW800968 | 233/D/0207 | 233/D/0207 |  | SO on sewer network | NZ1148064300 | GB103023075801 | Tyne from Watersmeet to Tidal Limit | TYNE |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 98.53%
Northumbrian Water | MID TYNE SEWERAGE SCHEME CSO | 6NW800986 | 233/B/0113 | 233/B/0113 |  | SO on sewer network | NZ1207064671 | 8 | #N/A | RIVER TYNE |  |  | Commissioned pre-2016 - full year data expected | 0.5 | 2 | 80.76% | Comms failure / issue | Resolved - December
Northumbrian Water | MILFIELD SEWAGE TREATMENT WORKS | 6NW800817 | 210/1327 | 210/1327 | 210/1327-02 | Storm tank at WwTW | NT9388034340 | GB102021073050 | Till from Glen to River Tweed | UNNAMED TRIB RIVER TILL |  |  | EDM to be installed by December 2023 | #N/A | #N/A | #N/A
Northumbrian Water | MILK MARKET PUMPING STATION | 6NW800532 | 235/1115 | 235/1115 |  | Storm discharge at pumping station | NZ2551063930 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | MILL COTTAGE CSO | 6NW800887 | 232/1000 | 232/1000 |  | SO on sewer network | NY8305056660 | GB103023074710 | Allen from Source to West Allen | RIVER EAST ALLEN |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | MILL COTTAGES CSO | 6NW800922 | 241/1119 | 241/1119 |  | SO on sewer network | NZ0304136761 | GB103024077461 | Wear from Middlehope Burn to Houselop Beck | WEAR |  |  | Commissioned pre-2016 - full year data expected | 2.5 | 7 | 97.08%
Northumbrian Water | MILL FARM COMBINED SEWER OVERFLOW | 6NW801016 | 241/1121 | 241/1121 |  | SO on sewer network | NZ1707031805 | GB103024077390 | Beechburn Beck (Trib of Wear) | BEECHBURN BECK |  |  | Commissioned pre-2016 - full year data expected | 22.5 | 3 | 92.65%
Northumbrian Water | MILL LANE CSO | 6NW801652 | #TBC | Permit Anomaly | To be permitted for storm | SO on sewer network | NZ3187241798 | GB103024077490 | Old Durham Beck from Source to Pittington Beck | Sherburnhouse Beck |  |  | Commissioned pre-2016 - full year data expected | 5 | 8 | 99.83%
Northumbrian Water | MILL LANE CSO | 6NW801646 | 256/1063 | 256/1063 |  | SO on sewer network | NZ7115019350 | GB103025071950 | Kilton Beck from Middle Gill Beck to North Sea | SKINNINGROVE BECK |  |  | Commissioned pre-2016 - full year data expected | 312.5 | 58 | 99.75%
Northumbrian Water | MILL STRAND COMBINED SEWER OVERFLOW | 6NW800208 | 210/1348 | 210/1348 |  | SO on sewer network | NT9965052330 | GB510202110000 | TWEED | RIVER TWEED (SALINE ESTUARY) |  |  | Mar 2021 | #N/A | #N/A | 0% | Sensor failure / issue | Scheduled
Northumbrian Water | CSO AT MILL TERRACE | 6NW801505 | 25/04/1606 | 25/04/1606 |  | SO on sewer network | NZ3995023330 | GB103025072360 | Billingham Beck from Bishopton Bck to Brierle | THORPE BECK |  |  | Commissioned pre-2016 - full year data expected | 0.75 | 3 | 89.65% | Sensor failure / issue | Resolved - June
Northumbrian Water | MILLBURNGATE CSO | 6NW801266 | 245/1286 | 245/1286 |  | SO on sewer network | NZ2724742573 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | RIVER WEAR |  |  | Commissioned pre-2016 - full year data expected | 322.75 | 52 | 99.63%
Northumbrian Water | MILLFIELD CSO | 6NW801257 | 226/1105 | 226/1105 |  | SO on sewer network | NZ2627581226 | GB103022077052 | Blyth from Pont to Tidal Limit | BLYTH, TRIBUTARY OF |  |  | Commissioned pre-2016 - full year data expected | 10.5 | 18 | 99.98%
Northumbrian Water | MILLFIELD SPS | 6NW800455 | 210/A/0440 | 210/A/0440 | A1 | Storm discharge at pumping station | NT9762051540 | 3 | #N/A | TWEED, TRIBUTARY OF |  |  | Commissioned in 2019 - full year data expected | 35.1356 | 14 | 99.6%
Northumbrian Water | MILLHOUSE FARM CSO | 6NW800962 | 244/0917 | 244/0917 |  | SO on sewer network | NZ1177043450 | GB103024077310 | Browney from Source to Pan Burn | STEELEY BURN |  |  | Commissioned pre-2016 - full year data expected | 8 | 13 | 75.84% | Comms failure / issue | Scheduled
Northumbrian Water | MINDRUM TERRACE CSO | 6NW801437 | 235/1897 | 235/1897 |  | SO on sewer network | NZ3499167106 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 0.5 | 1 | 99.99%
Northumbrian Water | MINI GOLF CSO | 6NW800377 | 235/1797 | 235/1797 |  | SO on sewer network | NZ3487573880 | GB103022076180 | Brierdene Burn from Source to North Sea | NORTH SEA |  | Whitley Bay | Commissioned in 2019 - full year data expected | 6.4161 | 2 | 99.99%
Northumbrian Water | MITCHEL TERRACE CSO | 6NW801048 | 235/1822 | 235/1822 |  | SO on sewer network | NZ1688252309 | GB103023075670 | Team from Source to Tyne | KYO BURN (RIVER TEAM) |  |  | Commissioned pre-2016 - full year data expected | 80.75 | 31 | 74.8% | Comms failure / issue | Scheduled
Northumbrian Water | MITCHELL AVENUE SEWAGE PUMPING STAN | 6NW800470 | 221/1075 | 221/1075 | 221/1075-01 | Storm discharge at pumping station | NU2271032370 | GB620301100000 | Farne Islands to Newton Haven | NORTH SEA |  | Seahouses North | Commissioned in 2018 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | MITRE PLACE CSO | 6NW801471 | 235/1940 | 235/1940 |  | SO on sewer network | NZ3554066380 | GB510302310200 | TYNE | TYNE SALINE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 48.56% | Comms failure / issue | Resolved - October
Northumbrian Water | LUDWORTH SSO MOOR CRESCENT | 6NW801461 | 245/1256 | 245/1256 |  | SO on sewer network | NZ3587041270 | GB103024077490 | Old Durham Beck from Source to Pittington Beck | SHADFORTH BECK |  |  | Commissioned pre-2016 - full year data expected | 177 | 61 | 95.64% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: Cost beneficial outcome not yet determined
Northumbrian Water | MOOR LANE SSO | 6NW801013 | 226/0454 | 226/0454 |  | SO on sewer network | NZ1503072050 | GB103022076860 | Pont from Med Burn to Small Burn | PONT |  |  | Commissioned pre-2016 - full year data expected | 146.25 | 14 | 98.2%
Northumbrian Water | MOOR ROAD SOUTH CSO | 6NW801187 | 235/1959 | 235/1959 |  | SO on sewer network | NZ2468067410 | GB103023075780 | Ouse Burn from Source to Tyne | UNNAMED TRIB OF OUSE BURN |  |  | Commissioned pre-2016 - full year data expected | 3.75 | 3 | 78.93% | Comms failure / issue | Scheduled
Northumbrian Water | MOOR VIEW CSO | 6NW800882 | 232/1016 | 232/1016 |  | SO on sewer network | NY7413063810 | GB103023075532 | South Tyne from Tipalt Burn to Allen | MELKRIDGE BURN |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | MOORSHOLM SEWAGE TREATMENT WORKS | 6NW800199 | 25/06/1010 | 25/06/1010 | A2 | Inlet SO at WwTW | NZ6904015580 | GB103025071920 | Kilton Beck from Source to Middle Gill Beck | HAGG BECK (KILTON BECK TRIB) |  |  | Commissioned in 2020 - full year data expected | 317.065 | 46 | 92.05%
Northumbrian Water | MOORSIDE CSO DER002 | 6NW800231 | 234/1106 | 234/1106 |  | SO on sewer network | NZ0902849791 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | DENE BURN (RIVER DERWENT) |  |  | Commissioned in 2017 - full year data expected | 0 | 0 | 41.94% | Comms failure / issue | Resolved - December
Northumbrian Water | MORDON STW | 6NW800778 | 253/0065 | Permit Anomaly - STW permit 253/0065 | To be permitted for settled storm | Storm tank at WwTW | NZ3282326298 | GB103025072391 | Skerne form Woodham Burn to Demons Beck | River Skerne |  |  | Commissioned in 2020 - full year data expected | 268.4425 | 43 | 100%
Northumbrian Water | MORPETH CSO D TENTER TERRACE | 6NW000008 | 225/1075 | 225/1075 |  | SO on sewer network | NZ2016085840 | GB103022077061 | Wansbeck from Font to Bothal Burn | WANSBECK |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 97.35%
Northumbrian Water | MORPETH SEWAGE TREATMENT WORKS INLET CSO | 6NW800158 | 225/1036 | 225/1036 | A3 | Inlet SO at WwTW | NZ2086686427 | GB103022077061 | Wansbeck from Font to Bothal Burn | RIVER WANSBECK |  |  | Commissioned in 2020 - full year data expected | 37.8361 | 19 | 100%
Northumbrian Water | MORPETH SEWAGE TREATMENT WORKS Storm Tank | 6NW800204 | 225/1036 | 225/1036 | A2 | Storm tank at WwTW | NZ2086686427 | GB103022077061 | Wansbeck from Font to Bothal Burn | RIVER WANSBECK |  |  | Commissioned in 2020 - full year data expected | 382.8478 | 35 | 99.97%
Northumbrian Water | MOSTYN TERRACE CSO | 6NW800971 | 242/1030 | 242/1030 |  | SO on sewer network | NZ1257224018 | GB103024072690 | Gaunless from Source to Hummer Beck | UNNAMED TRIB RIVER GAUNLESS |  |  | Commissioned pre-2016 - full year data expected | 0.25 | 1 | 83.17% | Telemetry or data archiving failure / issue | Resolved - March
Northumbrian Water | MOUNT PLEASANT CSO (DER41) | 6NW801023 | 244/1020 | 244/1020 |  | SO on sewer network | NZ1639647567 | GB103024077330 | Smallhope Burn from Source to Browney, Stocke | SMALLHOPE BURN |  |  | Commissioned pre-2016 - full year data expected | 39 | 31 | 99.27%
Northumbrian Water | MOUNT ROAD CSO BT003 | 6NW800825 | 210/1358 | 210/1358 |  | SO on sewer network | NT9973552213 | GB510202110000 | TWEED | RIVER TWEED (SALINE ESTUARY) |  | Spittal | Commissioned pre-2016 - full year data expected | 34.4 | 46 | 99.73%
Northumbrian Water | MOUNTFORD ROAD CSO | 6NW801377 | 226/1195 | 226/1195 |  | SO on sewer network | NZ3071377117 | 363 | #N/A | UUNAMED TRIB OF LYSDON BURN |  |  | Commissioned pre-2016 - full year data expected | 47.75 | 21 | 99.99%
Northumbrian Water | MURTON COMBINED SEWER OVERFLOW | 6NW801499 | EPRCB3195RW | EPRCB3195RW |  | SO on sewer network | NZ3979646686 | GB103025075970 | Dalton Beck to North Sea | CULVERTED TRIB OF SEAHAM BURN |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | NAPIER COURT CSO | 6NW801119 | 235/1850 | 235/1850 |  | SO on sewer network | NZ2099959802 | GB103023075670 | Team from Source to Tyne | BLACK BURN |  |  | Commissioned pre-2016 - full year data expected | 1.25 | 1 | 98.48%
Northumbrian Water | NARROWGATE CSO | 6NW800855 | EPRAB3090RL | EPRAB3090RL |  | SO on sewer network | NU1859313478 | GB103022076350 | Aln from Edlingham Burn to Tidal Limit | UNNAMED TRIB OF RIVER ALN |  |  | Commissioned pre-2016 - full year data expected | 54 | 37 | 99.83%
Northumbrian Water | NEASHAM EJECTOR STATION SSO | 6NW800583 | 254/E/0204 | 254/E/0204 |  | Storm discharge at pumping station | NZ3270010200 | GB103025072595 | Tees from Skerne to Tidal Limit | TEES |  |  | Commissioned in 2020 - full year data expected | 65.2308 | 18 | 91.15%
Northumbrian Water | NEASHAM ROAD (Y4) CSO | 6NW800345 | EPRJB3293DK | EPRJB3293DK |  | SO on sewer network | NZ2912514232 | GB103025072596 | Skerne from Demons Beck to Tees | RIVER SKERNE |  |  | Commissioned in 2017 - full year data expected | 1.5 | 4 | 99.99%
Northumbrian Water | NEASHAM ROAD CSO (Y5) | 6NW801330 | EPRMB3892AA | EPRMB3892AA |  | SO on sewer network | NZ2912514232 | GB103025072596 | Skerne from Demons Beck to Tees | RIVER SKERNE |  |  | Commissioned pre-2016 - full year data expected | 9.75 | 15 | 56.74% | Comms failure / issue | Scheduled
Northumbrian Water | NELSON VILLAGE CSO | 6NW801217 | 226/1235 | 226/1235 |  | SO on sewer network | NZ2594278700 | GB103022077052 | Blyth from Pont to Tidal Limit | THE HORTON BURN (R BLYTH) |  |  | Commissioned pre-2016 - full year data expected | 209 | 33 | 99.99%
Northumbrian Water | NENTHEAD STW | 6NW800699 | 232/1097 | 232/1097 | A2 | Storm tank at WwTW | NY7768044300 | GB103023075420 | Nent from Source to South Tyne | RIVER NENT |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | NETHERTON CSO | 6NW800207 | 223/0872 | 223/0872 |  | SO on sewer network | NT9897807531 | GB103022076750 | Netherton Burn Catch (trib of Wreigh Burn) | NETHERTON BURN |  |  | Commissioned in 2018 - full year data expected | 6.75 | 3 | 51.01% | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
Northumbrian Water | NETHERTON PARK SPS | 6NW800526 | 226/1278 | 226/1278 | A1 | Storm discharge at pumping station | NZ2229080390 | GB103022077052 | Blyth from Pont to Tidal Limit | PEGWHISTLE BURN |  |  | Commissioned in 2019 - full year data expected | 779.6861 | 47 | 99.98%
Northumbrian Water | NETHERTON SEWAGE TREATMENT WORKS | 6NW800808 | 223/1000 | 223/1000 | 223/1000-02 | Inlet SO at WwTW | NT9921007480 | GB103022076750 | Netherton Burn Catch (trib of Wreigh Burn) | THE NETHERTON BURN |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | NEW COATHAM CSO REF L73 | 6NW801605 | 256/1065 | 256/1065 |  | SO on sewer network | NZ5981225474 | GB650301500005 | Tees Coastal | NORTH SEA |  | Redcar Coatham | Commissioned pre-2016 - full year data expected | 95.1667 | 26 | 96.67%
Northumbrian Water | NEW HALL FARM CSO | 6NW800848 | 223/0922 | 223/0922 |  | SO on sewer network | NU1319300547 | GB103022076693 | Coquet from Forest Burn to Tidal Limit | UNNAMED TRIB OF RIVER COQUET |  |  | Commissioned pre-2016 - full year data expected | 337.5 | 62 | 99.98% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: Cost beneficial outcome not yet determined
Northumbrian Water | NEW MARE CLOSE FARM CSO | 6NW801348 | NPSWQD006839 | NPSWQD006839 |  | SO on sewer network | NZ2924974917 | GB103022076190 | Seaton Burn from Source to Tidal Limit | SEATON BURN |  |  | Commissioned pre-2016 - full year data expected | 301.75 | 48 | 99.98%
Northumbrian Water | NEW MOORS SEWAGE TREATMENT WORKS | 6NW800734 | 242/A/0706 | 242/A/0706 | A2 | Storm tank at WwTW | NZ1694824152 | GB103024072680 | Hummer Beck from Source to Gaunless | HUMMER BECK |  |  | Commissioned in 2019 - full year data expected | 197.3769 | 105 | 95.88%
Northumbrian Water | NEW QUAY CSO NC058 | 6NW801479 | 235/1903 | 235/1903 |  | SO on sewer network | NZ3566367900 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 77.75 | 27 | 99.83%
Northumbrian Water | NEW ROAD CSO | 6NW801466 | 235/1572 | 235/1572 |  | SO on sewer network | NZ3543562358 | GB103023075690 | Don from Source to Tidal Limit | DON |  |  | Commissioned pre-2016 - full year data expected | 80 | 17 | 66.56% | Sensor failure / issue | Scheduled
Northumbrian Water | NEW WELBECK ROAD PUMPING STATION | 6NW801347 | 235/1755 | 235/1755 | 235/1755-01 | Storm discharge at pumping station | NZ2984264771 | GB510302310200 | TYNE | RIVER TYNE SALINE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 612 | 62 | 95.59% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | NEW YORK CSO | 6NW801417 | 235/1901 | 235/1901 |  | SO on sewer network | NZ3499167106 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 2.5 | 4 | 99.99%
Northumbrian Water | NEWBIGGIN SSO (WILKIE TERRACE) | 6NW801650 | 224/0881 | 224/0881 |  | SO on sewer network | NZ3163287760 | GB650301500002 | Tyne and Wear | NORTH SEA |  |  | Commissioned pre-2016 - full year data expected | 265.75 | 19 | 99.99%
Northumbrian Water | NEWBIGGIN SEWAGE TREATMENT WORKS | 6NW800172 | 225/1031 | 225/1031 | A2 | Inlet SO at WwTW | NZ3238286215 | GB650301500002 | Tyne and Wear | NORTH SEA |  | Newbiggin North & Newbiggin South | Commissioned in 2019 - full year data expected | 94.4003 | 8 | 0.005327% | Installation set-up/design issue | Resolved - December
Northumbrian Water | NEWBIGGIN SEWAGE TREATMENT WORKS | 6NW800173 | 225/1031 | 225/1031 | A3 | Inlet SO at WwTW | NZ3129786715 | GB650301500002 | Tyne and Wear | NORTH SEA |  | Newbiggin North & Newbiggin South | Commissioned in 2018 - full year data expected | 861.1686 | 106 | 100%
Northumbrian Water | NEWBROUGH PUMPING STATION | 6NW800492 | 232/0969 | 232/0969 | A | Storm discharge at pumping station | NY8746067440 | GB103023075560 | Newbrough Burn Catchment (trib of South Tyne) | NEWBROUGH BURN (SOUTH TYNE) |  |  | Commissioned in 2020 - full year data expected | 66.3969 | 29 | 100%
Northumbrian Water | BURWELL AVENUE CSO | 6NW000009 | 235/1877 | 235/1877 |  | SO on sewer network | NZ1965063980 | GB510302310200 | TYNE | RIVER TYNE SALINE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 212.25 | 45 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | NEWBURN HAUGH/RIVERSDALE WAY P STN | 6NW801069 | 235/1731 | 235/1731 | 235/1731-01 | Storm discharge at pumping station | NZ1845963698 | GB510302310200 | TYNE | RIVER TYNE SALINE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 51.5 | 11 | 78.22% | Sensor failure / issue | Resolved - October
Northumbrian Water | NEWBURN INDUSTRIAL ESTATE P STN | 6NW800514 | 235/1732 | 235/1732 | 235/1732-01 | Storm discharge at pumping station | NZ1718064820 | GB510302310200 | TYNE | RIVER TYNE SALINE ESTUARY |  |  | Commissioned in 2020 - full year data expected | 0 | 0 | 99.97%
Northumbrian Water | NEWBURN PUMPING STATION | 6NW800510 | 233/1163 | 233/1163 | 233/1163-01 | Storm discharge at pumping station | NZ1663065310 | GB510302310200 | TYNE | RIVER TYNE SALINE ESTUARY |  |  | Commissioned in 2020 - full year data expected | 49.1836 | 20 | 100%
Northumbrian Water | NEWCASTLE UPON TYNE CSO ST ANNES WHARF | 6NW800319 | EPRCB3097AS | EPRCB3097AS |  | SO on sewer network | NZ2579864070 | 8 | #N/A | RIVER TYNE (TIDAL) |  |  | Commissioned in 2019 - full year data expected | 578.2667 | 89 | 98.05%
Northumbrian Water | NEWFIELD FARM CSO (NEW FIELD CSO 1) | 6NW801106 | EPRCB3191WN | EPRCB3191WN |  | SO on sewer network | NZ2037433890 | GB103024077464 | Wear from Gaunless to Browney | SEASONALLY DRY DITCH TO R.WEAR |  |  | Commissioned pre-2016 - full year data expected | 0.5 | 2 | 99.99%
Northumbrian Water | NEWFIELD STW | 6NW800745 | 243/1015 | 243/1015 | 243/1015-02 | Storm tank at WwTW | NZ2004033530 | GB103024077464 | Wear from Gaunless to Browney | WEAR |  |  | Commissioned in 2020 - full year data expected | 22.7125 | 57 | 89.65% | Installation set-up/design issue | Resolved - March
Northumbrian Water | NEWHOLME C.S.O. | 6NW800996 | 25/02/1103 | 25/02/1103 |  | SO on sewer network | NZ1432016920 | GB103025072190 | Tees from River Greta to River Skerne | UNNAMED TRIB OF TEES |  |  | Commissioned pre-2016 - full year data expected | 0.25 | 1 | 99.82%
Northumbrian Water | NEWPORT ROAD CSO | 6NW800427 | 254/1863 | 254/1863 |  | SO on sewer network | NZ4791719967 | GB510302509900 | TEES | RIVER TEES ESTUARY |  |  | Commissioned in 2019 - full year data expected | 43.7175 | 30 | 100%
Northumbrian Water | NEWPORT SEWAGE PUMPING STATION | 6NW800642 | 254/0255 | 254/0255 | 254/0255-01 | Storm discharge at pumping station | NZ4714020742 | 10 | #N/A | BILLINGHAM BECK |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | NEWTON STREET CSO | 6NW800293 | 235/1367 | 235/1367 |  | SO on sewer network | NZ2294162719 | GB510302310200 | TYNE | TYNE |  |  | Commissioned in 2019 - full year data expected | 0.00055556 | 1 | 100%
Northumbrian Water | NICKY NACK PUMPING STATION | 6NW800535 | 243/0933 | 243/0933 | 243/0933-01 | Storm discharge at pumping station | NZ2646036670 | GB103024077464 | Wear from Gaunless to Browney | NICKY NACK BECK |  |  | Commissioned in 2020 - full year data expected | 61.0031 | 18 | 100%
Northumbrian Water | NIGHTINGALE PLACE CSO | 6NW801644 | 245/1311 | 245/1311 |  | SO on sewer network | NZ2075951817 | GB103024077590 | Twizell Burn from Source to Cong Burn | STANLEY BURN, TRIBUTARY OF |  |  | Commissioned pre-2016 - full year data expected | 345.25 | 66 | 99.59% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | NO2 ESKDALE GARDENS CSO | 6NW801241 | 235/1442 | 235/1442 |  | SO on sewer network | NZ2580559497 | GB103023075670 | Team from Source to Tyne | TEAM |  |  | Commissioned pre-2016 - full year data expected | 86.25 | 46 | 97.21%
Northumbrian Water | 20 DERWENT DALE CUTLERS RD CSO | 6NW800949 | 234/1113 | 234/1113 |  | SO on sewer network | NZ0901752447 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | RIVER DERWENT |  |  | Commissioned pre-2016 - full year data expected | 1.5 | 4 | 93.76%
Northumbrian Water | NORHAM SEWAGE TREATMENT WORKS | 6NW800686 | 210/1328 | 210/1328 | 210/1328-04 | Storm tank at WwTW | NT9025047620 | 437 | #N/A | RIVER TWEED |  |  | Commissioned in 2020 - full year data expected | 2655.5294 | 145 | 100%
Northumbrian Water | NORTH BLYTH PUMPING STATION | 6NW800576 | 226/1156 | 226/1156 | 226/1156-01 | Storm discharge at pumping station | NZ3052283146 | GB510302203200 | BLYTH (N) | BLYTH SALINE ESTUARY |  |  | Commissioned in 2020 - full year data expected | 59.2156 | 21 | 100%
Northumbrian Water | NORTH CAMBOIS PUMPING STATION | 6NW800577 | 226/1155 | 226/1155 | 226/1155-01 | Storm discharge at pumping station | NZ3091084260 | GB650301500002 | Tyne and Wear | NORTH SEA |  |  | Commissioned in 2020 - full year data expected | 19.1289 | 7 | 82.76% | Comms failure / issue | Resolved - September
Northumbrian Water | NORTH GOSFORTH CSO | 6NW801189 | 226/1253 | 226/1253 |  | SO on sewer network | NZ2487072379 | GB103022076190 | Seaton Burn from Source to Tidal Limit | SEATON BURN |  |  | Commissioned pre-2016 - full year data expected | 71.25 | 28 | 99.96%
Northumbrian Water | NORTH GROYNE PUMPING STATION | 6NW800601 | 235/1481 | 235/1481 | A | Storm discharge at pumping station | NZ3649068480 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | Commissioned in 2020 - full year data expected | 13.65 | 13 | 100%
Northumbrian Water | NORTH HYLTON SEWAGE PUMPING STATION | 6NW800596 | 245/0938 | 245/0938 | 245/0938-01 | Storm discharge at pumping station | NZ3529657328 | GB510302402900 | WEAR | WEAR (TIDAL) |  |  | Commissioned in 2020 - full year data expected | 129.5897 | 28 | 100%
Northumbrian Water | NORTH PARADE HIGH LEVEL CSO (A52) | 6NW800384 | 235/1795 | 235/1795 |  | SO on sewer network | NZ3575072427 | GB650301500002 | Tyne and Wear | NORTH SEA |  | Whitley Bay | Commissioned in 2019 - full year data expected | 31.2122 | 4 | 100%
Northumbrian Water | NORTH POINT CSO | 6NW800393 | 235/1987 | 235/1987 |  | SO on sewer network | NZ3655070980 | GB650301500002 | Tyne and Wear | NORTH SEA |  | Cullercoats | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
Northumbrian Water | 20 WANSBECK STREET NORTH SEATON | 6NW801353 | 225/1063 | 225/1063 |  | SO on sewer network | NZ2944085393 | GB510302210100 | WANSBECK | WANSBECK ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 0.25 | 1 | 95.51%
Northumbrian Water | NORTH SEATON LEVEL CROSSING CSO | 6NW800337 | 225/1020 | 225/1020 |  | SO on sewer network | NZ2773285873 | GB103022077062 | Wansbeck from Bothal Burn to North Sea | RIVER WANSBECK(SALINE ESTUARY) |  |  | Commissioned in 2019 - full year data expected | 275.5 | 54 | 99.99%
Northumbrian Water | NORTH TEES SEWAGE PUMPING STATION Stockton east CSO | 6NW800639 | 254/0057 | 254/0057 | 254/0057-01 | SO on sewer network | NZ4660020100 | GB103025072550 | Lustrum Beck Catchment (trib of Tees) | LUSTRUM BECK |  |  | Commissioned in 2020 - full year data expected | 128.4742 | 25 | 100%
Northumbrian Water | WYLAM NORTH SPS CSO | 6NW800970 | 233/D/0206 | 233/D/0206 | A1 | Storm discharge at pumping station | NZ1182264535 | GB103023075801 | Tyne from Watersmeet to Tidal Limit | TYNE |  |  | Commissioned pre-2016 - full year data expected | 77.7667 | 40 | 99.61% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | NORTHSIDE PLACE CSO | 6NW801398 | 226/1264 | 226/1264 |  | SO on sewer network | NZ3112074340 | GB103022076190 | Seaton Burn from Source to Tidal Limit | SEATON BURN |  |  | Commissioned pre-2016 - full year data expected | 0.25 | 1 | 99.47%
Northumbrian Water | NORTON SEWAGE PUMPING STATION | 6NW800633 | 254/B/0252 | 254/B/0252 | A1 | Storm discharge at pumping station | NZ4550021400 | 10 | #N/A | BILLINGHAM BECK |  |  | Commissioned in 2020 - full year data expected | 256.4589 | 26 | 99.95%
Northumbrian Water | NUNTHORPE NO 1 SPS | 6NW800668 | 25/04/1621 | 25/04/1621 | A1 | Storm discharge at pumping station | NZ5318013830 | GB103025072210 | Marton West Beck Catchment (trib of Tidal Tees) | UNNAMED TRIB MARTON WEST BECK |  |  | Commissioned in 2020 - full year data expected | 540.7642 | 39 | 100%
Northumbrian Water | OAK ROAD CSO | 6NW801612 | 256/1064 | 256/1064 |  | SO on sewer network | NZ6176024160 | GB650301500005 | Tees Coastal | NORTH SEA |  | Redcar Stray | Commissioned pre-2016 - full year data expected | 0 | 0 | 97.72%
Northumbrian Water | OAKENSHAW CSO | 6NW801110 | 243/1005 | 243/1005 |  | SO on sewer network | NZ2025036950 | GB103024077464 | Wear from Gaunless to Browney | PARK HOUSE GILL |  |  | Commissioned pre-2016 - full year data expected | 1.25 | 4 | 99.99%
Northumbrian Water | OAKFIELD ROAD CSO | 6NW801577 | 254/1207 | 254/1207 |  | SO on sewer network | NZ5091219502 | GB103025072210 | Marton West Beck Catchment (trib of Tidal Tees) | ORMESBY BECK |  |  | Commissioned pre-2016 - full year data expected | 6 | 3 | 99.99%
Northumbrian Water | OAKLEY GREEN CSO | 6NW801637 | #TBC | Permit Anomaly | To be permitted for storm | SO on sewer network | NZ1868726495 | GB103024072690 | Gaunless from Source to Hummer Beck | River Gaunless |  |  | Commissioned pre-2016 - full year data expected | 72.5 | 33 | 76.65% | Comms failure / issue | Resolved - November
Northumbrian Water | OAKS FIELD CSO | 6NW801089 | 235/1710 | 235/1710 |  | SO on sewer network | NZ1929053510 | GB103023075670 | Team from Source to Tyne | HOUGHWELL BURN |  |  | Commissioned pre-2016 - full year data expected | 69.5 | 16 | 99.89%
Northumbrian Water | OGLE SEWAGE TREATMENT WORKS | 6NW800729 | 226/0141 | Permit Anomaly - STW permit 226/0141 | To be permitted for settled storm | Storm tank at WwTW | NZ1401878610 | GB103022076900 | Ogle Burn Catchment (trib of Blyth) | Ogle Burn |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | OPP OLD CASTLESIDE STW CSO | 6NW800936 | 234/1135 | 234/1135 |  | SO on sewer network | NZ0724049100 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | WHARNLEY BURN (DERWENT) |  |  | Commissioned pre-2016 - full year data expected | 4.75 | 9 | 99.97%
Northumbrian Water | OLD CLEATLAM STW | 6NW800721 | 252/0060 | Permit Anomaly - STW permit 252/0060 | To be permitted for settled storm | Storm tank at WwTW | NZ1213119704 | GB103025072270 | Sudburn Beck from Source to Langley Beck | Sudburn Beck |  |  | Feb 2021 | 29.4775 | 23 | 98.15%
Northumbrian Water | CORNFORTH PUMPING STATION | 6NW801379 | 243/0602 | 243/0602 | 243/0602-01 | Storm discharge at pumping station | NZ3151634799 | GB103024077410 | Croxdale Beck from Source to Wear | COXHOE BECK |  |  | Commissioned pre-2016 - full year data expected | 117.5 | 26 | 99.92%
Northumbrian Water | OLD DERWENT BRIDGE CSO | 6NW800206 | 234/0904 | 234/0904 |  | SO on sewer network | NZ1983062380 | GB510302310200 | TYNE | DERWENT (TIDAL) |  |  | Commissioned pre-2016 - full year data expected | 66 | 22 | 99.78%
Northumbrian Water | LONGFRAMLINGTON SSO OLD HALL | 6NW800849 | 223/G/0102 | 223/G/0102 |  | SO on sewer network | NU1340001500 | GB103022076660 | Swarland Burn Catchment (trib of Coquet) | FENCE BURN |  |  | Commissioned pre-2016 - full year data expected | 82.5 | 13 | 51.45% | Comms failure / issue | Scheduled
Northumbrian Water | OLD RIVER TEES PUMPING STATION | 6NW800638 | 254/1937 | 254/1937 |  | Storm discharge at pumping station | NZ4686018560 | GB510302509900 | TEES | OLD RIVER TEES |  |  | Commissioned in 2018 - full year data expected | 103.2586 | 39 | 100%
Northumbrian Water | OLD TYNE BRIDGE CSO | 6NW800874 | 232/1166 | 232/1166 |  | SO on sewer network | NY7056663780 | GB103023075532 | South Tyne from Tipalt Burn to Allen | RIVER SOUTH TYNE |  |  | Commissioned pre-2016 - full year data expected | 55 | 53 | 96.7% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution
Northumbrian Water | SEWAGE PUMPING STATION AT SITE OF OLD YARM STW | 6NW800614 | 254/1092 | 254/1092 | A (Settled storm) | Storm discharge at pumping station | NZ4041011610 | GB103025072595 | Tees from Skerne to Tidal Limit | TEES ESTUARY (FRESHWATER) |  |  | Commissioned pre-2016 - full year data expected | 315.75 | 27 | 99.99%
Northumbrian Water | OLIVER STREET CSO | 6NW801086 | 245/1265 | 245/1265 |  | SO on sewer network | NZ1906251851 | GB103024077590 | Twizell Burn from Source to Cong Burn | TRIP OF STANLEY BURN |  |  | Commissioned pre-2016 - full year data expected | 2.75 | 4 | 72.69% | Comms failure / issue | Scheduled
Northumbrian Water | OPPOSITE 16 FRONT STREET CSO | 6NW801138 | EPRBB3899DP | EPRBB3899DP |  | SO on sewer network | NZ2150145218 | GB103024077551 | Browney from Smallhope Burn Deerness confl | RIVER BROWNEY |  |  | Commissioned pre-2016 - full year data expected | 29.25 | 24 | 99.99%
Northumbrian Water | OSMAN TERRACE CSO | 6NW801658 | 245/1378 | 245/1378 |  | SO on sewer network | NZ3249350763 | GB103024077580 | Lumley Park Burn from Source to Herrington Burn | MOORS BURN |  |  | Commissioned pre-2016 - full year data expected | 15.25 | 7 | 99.99%
Northumbrian Water | OTTERBURN CRESCENT CSO | 6NW801429 | 245/1367 | 245/1367 |  | SO on sewer network | NZ3291950302 | GB103024077580 | Lumley Park Burn from Source to Herrington Burn | MOORS BURN TRIB |  |  | Commissioned pre-2016 - full year data expected | 1.25 | 2 | 98.5%
Northumbrian Water | OTTERBURN STW | 6NW800806 | 231/1087 | 231/1087 | 231/1087-02 | Storm tank at WwTW | NY8913092600 | GB103023075320 | Rede from Bellshiel Burn to N Tyne | RIVER REDE |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | OUSE BURN CSO NO 8 | 6NW801248 | 235/F/0346C | 235/F/0346 |  | SO on sewer network | NZ2609565199 | GB103023075780 | Ouse Burn from Source to Tyne | OUSE BURN |  |  | Commissioned pre-2016 - full year data expected | 0.1 | 1 | 100%
Northumbrian Water | OUSEBURN EAST PS | 6NW800539 | 235/1825 | 235/1825 | 235/1825-01 | Storm discharge at pumping station | NZ2647064090 | GB510302310200 | TYNE | RIVER TYNE SALINE ESTUARY |  |  | Commissioned in 2020 - full year data expected | 125.0839 | 44 | 100%
Northumbrian Water | OUSEBURN WEST PS | 6NW800538 | 235/1824 | 235/1824 | 235/1824-01 | Storm discharge at pumping station | NZ2641064080 | GB510302310200 | TYNE | RIVER TYNE SALINE ESTUARY |  |  | Commissioned in 2020 - full year data expected | 656.4753 | 67 | 100%
Northumbrian Water | OUSTON VILLA FARM CSO | 6NW801236 | 235/1878 | 235/1878 |  | SO on sewer network | NZ2648053780 | GB103023075670 | Team from Source to Tyne | ROWLETCH BURN 9RIVER TEAM) |  |  | Commissioned pre-2016 - full year data expected | 76.25 | 17 | 99.98%
Northumbrian Water | OUTLET LANE CSO NO.2 | 6NW800899 | 233/1050 | 233/1050 |  | SO on sewer network | NY9412064400 | GB103023075801 | Tyne from Watersmeet to Tidal Limit | RIVER TYNE TRIBUTARY |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.72%
Northumbrian Water | OUTLET ROAD NO 2 CSO | 6NW800900 | 233/1240 | 233/1240 |  | SO on sewer network | NY9437064150 | GB103023075801 | Tyne from Watersmeet to Tidal Limit | TYNE |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.89%
Northumbrian Water | OVINGHAM PUMPING STATION CSO | 6NW800500 | 233/G/0328 | 233/G/0328 | A1 | Storm discharge at pumping station | NZ0840263635 | GB103023075770 | Whittle Burn Catchment (trib of Tyne) | WHITTLE BURN, TRIB OF TYNE |  |  | Commissioned pre-2016 - full year data expected | 146.25 | 23 | 81.94% | Comms failure / issue | Resolved - December
Northumbrian Water | OVINGTON STW | 6NW800151 | 252/0366 | 252/0366 | A2 | Inlet SO at WwTW | NZ1330315050 | GB103025072190 | Tees from River Greta to River Skerne | TEES |  |  | Commissioned in 2020 - full year data expected | 0.12278 | 5 | 99.3%
Northumbrian Water | OVINGTON CSO TD034 | 6NW800933 | 233/1248 | 233/1248 |  | SO on sewer network | NZ0685463561 | GB103023075801 | Tyne from Watersmeet to Tidal Limit | TRIB COCKERMERE BURN |  |  | Commissioned pre-2016 - full year data expected | 359.8667 | 58 | 96.13%
Northumbrian Water | OWEN BRANNIGAN DRIVE CSO | 6NW801255 | 226/1260 | 226/1260 |  | SO on sewer network | NZ2686273529 | GB103022076190 | Seaton Burn from Source to Tidal Limit | SEATON BURN |  |  | Commissioned pre-2016 - full year data expected | 16.75 | 4 | 72.7% | Comms failure / issue | Resolved - October
Northumbrian Water | OWTON MANOR LANE CSO | 6NW801578 | Not on public register | QR.25/05/5014 |  | SO on sewer network | NZ5009029567 | 368 | #N/A | Culverted Watercourse into Stream |  | Seaton Carew (Centre) | Commissioned pre-2016 - full year data expected | 0.1 | 1 | 99.09%
Northumbrian Water | OXBRIDGE LANE CSO | 6NW801538 | 254/1835 | 254/1835 |  | SO on sewer network | NZ4305018748 | GB103025072550 | Lustrum Beck Catchment (trib of Tees) | THE LUSTRUM BECK |  |  | Commissioned pre-2016 - full year data expected | 124.5 | 20 | 99.6%
Northumbrian Water | PALACE STREET NORTH CSO 1 | 6NW800834 | 210/1361 | 210/1361 |  | SO on sewer network | NT9993852464 | GB510202110000 | TWEED | Tweed Estuary |  | Spittal | Commissioned pre-2016 - full year data expected | 8 | 25 | 99.99%
Northumbrian Water | PALACE STREET NORTH CSO 2 | 6NW800833 | 210/1357 | 210/1357 |  | SO on sewer network | NT9993852464 | GB510202110000 | TWEED | RIVER TWEED (SALINE ESTUARY) |  | Spittal | Commissioned pre-2016 - full year data expected | 7.6333 | 24 | 99.98%
Northumbrian Water | PALLION PUMPING STATION | 6NW800604 | 245/1210 | 245/1210 | 245/1210-01 | Storm discharge at pumping station | NZ3770057990 | GB510302402900 | WEAR | RIVER WEAR (SALINE ESTUARY) |  |  | Commissioned pre-2016 - full year data expected | 77.25 | 47 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | PALM TERRACE CSO | 6NW800255 | 235/1717 | 235/1717 |  | SO on sewer network | NZ1851054810 | GB103023075670 | Team from Source to Tyne | FARLIETH BURN |  |  | Commissioned pre-2016 - full year data expected | 1.5 | 2 | 99.52%
Northumbrian Water | PARADISE FARM (WILLOW FARM) CSO | 6NW801382 | 243/0988 | 243/0988 | A1 | Storm discharge at pumping station | NZ3141736206 | GB103024077410 | Croxdale Beck from Source to Wear | COXHOE BECK TRIB |  |  | Commissioned pre-2016 - full year data expected | 169 | 39 | 99.98%
Northumbrian Water | PARADISE FARM CSO | 6NW801546 | 255/1217 | 255/1217 |  | SO on sewer network | NZ4341043110 | 367 | #N/A | HORDEN BURN |  |  | Commissioned pre-2016 - full year data expected | 223.5 | 60 | 99.83% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution
Northumbrian Water | PARK HEAD STORAGE TANK CSO | 6NW800286 | 242/1044 | 242/1044 |  | SO on sewer network | NZ2300030510 | GB103024072730 | Gaunless from Hummer Beck to Wear | COUNDON BURN |  |  | Commissioned pre-2016 - full year data expected | 386 | 45 | 99.65%
Northumbrian Water | PARK HILL CSO | 6NW801381 | 243/1013 | 243/1013 |  | SO on sewer network | NZ3140036250 | GB103024077410 | Croxdale Beck from Source to Wear | COXHOE BECK |  |  | Commissioned pre-2016 - full year data expected | 30.75 | 23 | 99.63%
Northumbrian Water | PARK LANE CSO | 6NW800438 | 256/1080 | 256/1080 |  | SO on sewer network | NZ6041515706 | GB103025071970 | Skelton Beck Catch (Saltburn) trib of North Sea | CHAPEL BECK |  |  | Commissioned in 2019 - full year data expected | 26.8022 | 20 | 100%
Northumbrian Water | PARK ROAD & GREEN LANE CSO | 6NW801260 | 225/G/0361 | 225/G/0361 |  | SO on sewer network | NZ2708086616 | GB103022077062 | Wansbeck from Bothal Burn to North Sea | WANSBECK, TRIBUTARY OF |  |  | Commissioned pre-2016 - full year data expected | 10.25 | 11 | 91.69%
Northumbrian Water | PARK ROAD CSO | 6NW801311 | NPSWQD009544 | NPSWQD009544 |  | SO on sewer network | NZ2836950977 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | RIVER WEAR |  |  | Commissioned pre-2016 - full year data expected | 215.75 | 40 | 99.94%
Northumbrian Water | PARK ROAD CSO WV41 | 6NW800247 | 241/1034 | 241/1034 |  | SO on sewer network | NZ1715129940 | GB103024077462 | Wear from Houselop Beck to Beechburn Beck | RIVER WEAR TRIBUTARY |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 90.95%
Northumbrian Water | PARK ROAD NORTH CSO | 6NW801668 | 245/1264 | 245/1264 |  | SO on sewer network | NZ2824052410 | GB103024077624 | Wear DS of Lumley Park Burn to Tidal Limit | TRIBUTARY OF RIVER WEAR |  |  | Commissioned pre-2016 - full year data expected | 12.75 | 15 | 99.99%
Northumbrian Water | PARKGATE FARM CSO | 6NW801066 | 234/1131 | 234/1131 |  | SO on sewer network | NZ1822861510 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | DERWENT TRIB |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 48.42% | Comms failure / issue | N/A - Ongoing investigation
Northumbrian Water | PASTURE LANE CSO | 6NW801600 | 25/04/1776 | 25/04/1776 |  | SO on sewer network | NZ5717720096 | GB103025072320 | Tees Estuary (S Bank) | UNNAMED TRIB OF DABHOLME BECK |  |  | Commissioned pre-2016 - full year data expected | 52.25 | 19 | 99.95%
Northumbrian Water | PATTON STREET STORAGE TANK | 6NW800398 | 255/1193 | 255/1193 |  | SO on sewer network | NZ3828039670 | GB103025075930 | Castle Eden Burn from Source to North Sea | TRIB. OF GORE BURN |  |  | Commissioned in 2020 - full year data expected | 0 | 0 | 2.377% | Comms failure / issue | N/A - Ongoing investigation
Northumbrian Water | 20 PEARSON STREET CSO SE 009 | 6NW801224 | 243/1000 | 243/1000 |  | SO on sewer network | NZ2837033580 | GB103024077410 | Croxdale Beck from Source to Wear | EAST HOWLE BECK, TRIBUTARY OF |  |  | Commissioned pre-2016 - full year data expected | 0.25 | 1 | 99.99%
Northumbrian Water | PEASES WEST CSO | 6NW801021 | 241/1083 | 241/1083 |  | SO on sewer network | NZ1630636236 | GB103024077390 | Beechburn Beck (Trib of Wear) | CROOK BECK |  |  | Commissioned pre-2016 - full year data expected | 338.75 | 41 | 81.74% | Comms failure / issue | Scheduled | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution
Northumbrian Water | PEGSWOOD CSOCOUNTY FIRST SCHOOL | 6NW801153 | EPRCB3192AA | EPRCB3192AA |  | SO on sewer network | NZ2266587950 | GB103022077030 | Bothal Burn Catchment (trib of Wansbeck) | TRIBUTARY OF THE BOTHAL BURN |  |  | Commissioned pre-2016 - full year data expected | 11 | 19 | 99.99%
Northumbrian Water | PEGSWOOD STW | 6NW800755 | 225/1079 | 225/1079 | A2 | Storm tank at WwTW | NZ2337187452 | GB103022077030 | Bothal Burn Catchment (trib of Wansbeck) | BOTHAL BURN |  |  | Commissioned in 2020 - full year data expected | 285.6125 | 28 | 100%
Northumbrian Water | PELAW BANK CSO CH57 | 6NW801280 | 245/1323 | 245/1323 |  | SO on sewer network | NZ2740751630 | GB103024077600 | Cong Burn from Twizell Burn to Wear | CHESTER BURN |  |  | Commissioned pre-2016 - full year data expected | 213 | 57 | 96.35% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | PELAW WOOD ST. GILES CLOSE CSO | 6NW801299 | EPRBB3691AB | EPRBB3691AB |  | SO on sewer network | NZ2851242518 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | PELAW WOOD BECK |  |  | Commissioned in 2017 - full year data expected | 1.25 | 1 | 97.53%
Northumbrian Water | PELTON CSO | 6NW801203 | 245/E/0391 | 245/E/0391 |  | SO on sewer network | NZ2536552618 | GB103024077600 | Cong Burn from Twizell Burn to Wear | STELLA GILL |  |  | Commissioned pre-2016 - full year data expected | 1.75 | 4 | 99.99%
Northumbrian Water | WHELDON TERRACE CSO | 6NW000010 | EPRAB3894VG | EPRAB3894VG |  | SO on sewer network | NZ2536252629 | GB103024077600 | Cong Burn from Twizell Burn to Wear | TRIBUTARY OF THE CHESTER BURN |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | PELTON FELL ROAD 3 CSO CH14 | 6NW801202 | 245/1314 | 245/1314 |  | SO on sewer network | NZ2589751664 | GB103024077600 | Cong Burn from Twizell Burn to Wear | CHESTER BURN |  |  | Commissioned pre-2016 - full year data expected | 186.5 | 62 | 98.44%
Northumbrian Water | PELTON FELL ROAD CSO | 6NW801235 | 245/1335 | 245/1335 |  | SO on sewer network | NZ2677251763 | GB103024077600 | Cong Burn from Twizell Burn to Wear | CHESTER BURN |  |  | Commissioned pre-2016 - full year data expected | 160.5 | 43 | 99.91%
Northumbrian Water | PENNINE VIEW CSO | 6NW800238 | 234/1161 | 234/1161 |  | SO on sewer network | NZ1173457950 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | TRIBUTARY OF RIVER DERWENT |  |  | Commissioned pre-2016 - full year data expected | 115.25 | 33 | 99.75%
Northumbrian Water | PERCY MAIN CSO | 6NW801438 | 235/1900 | 235/1900 |  | SO on sewer network | NZ3499167106 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 5.75 | 7 | 99.99%
Northumbrian Water | PERCY ROAD HIGH LEVEL CSO | 6NW800385 | 235/1794 | 235/1794 |  | SO on sewer network | NZ3596172285 | GB650301500002 | Tyne and Wear | NORTH SEA |  | Whitley Bay | Commissioned pre-2016 - full year data expected | 0 | 0 | 69.21% | Comms failure / issue | Resolved - April
Northumbrian Water | PESSPOOL LANE CSO | 6NW800400 | 255/1179 | 255/1179 |  | SO on sewer network | NZ3852843622 | GB103024077540 | Pittington Beck from Coalford to Old Durham Beck | CALDWELL BURN |  |  | Commissioned pre-2016 - full year data expected | 742.8333 | 50 | 99.89%
Northumbrian Water | PETH HEAD PS | 6NW800684 | 233/0993 | Permit Anomaly - EO permit 233/0993 | To be permitted for storm | Storm discharge at pumping station | NY9433864182 | GB103023075801 | Tyne from Watersmeet to Tidal Limit | River Tyne |  |  | Commissioned in 2020 - full year data expected | 80.1733 | 41 | 99.95%
Northumbrian Water | PHILIPBURN DENE PS | 6NW800491 | 232/A/1011 | 232/A/1011 | A1 | Storm discharge at pumping station | NY8403056200 | GB103023074710 | Allen from Source to West Allen | PHILIP BURN |  |  | Commissioned in 2020 - full year data expected | 17.8792 | 13 | 100%
Northumbrian Water | PHILLIPSON STREET ROSEHILL CSO | 6NW801396 | EPRBB3897EY | EPRBB3897EY |  | SO on sewer network | NZ3205866105 | 8 | #N/A | RIVER TYNE |  |  | Commissioned in 2018 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | PILOT STREET PUMPING STATION | 6NW800602 | 235/0076 | 235/0076 | 235/0076-01 | Storm discharge at pumping station | NZ3662968240 | GB510302310200 | TYNE | TYNE |  |  | Commissioned in 2020 - full year data expected | 12.7889 | 12 | 99.97%
Northumbrian Water | PINEWOOD GARDENS CSO | 6NW801163 | 235/1968 | 235/1968 |  | SO on sewer network | NZ2409059830 | GB103023075670 | Team from Source to Tyne | BLACK BURN |  |  | Commissioned pre-2016 - full year data expected | 49 | 34 | 99.79%
Northumbrian Water | PIPEWELLGATE PUMPING STATION | 6NW801212 | 235/1664 | 235/1664 | 235/1664-01 | Storm discharge at pumping station | NZ2520063600 | GB510302310200 | TYNE | TYNE SALINE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | PITHOUSE LANE CSO (WEST RAINTON 5) | 6NW801385 | EPRGB3599NT | EPRGB3599NT |  | SO on sewer network | NZ3011646522 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | UNNAMED TRIB OF RIVER WEAR |  |  | Commissioned pre-2016 - full year data expected | 74.5 | 39 | 85.48% | Comms failure / issue | Scheduled | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | PITTINGTON STW | 6NW800782 | 245/0842 | 245/0842 |  | Storm tank at WwTW | NZ3322843765 | GB103024077540 | Pittington Beck from Coalford to Old Durham Beck | COALFORD BECK |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation | Performance - Infiltration
Northumbrian Water | PITY ME ROUNDABOUT CSO | 6NW801231 | 245/1354 | 245/1354 |  | SO on sewer network | NZ2639045940 | GB103024077622 | Blackdene Burn to confluence with Wear | PITY ME BECK |  |  | Commissioned pre-2016 - full year data expected | 20.75 | 14 | 98.41%
Northumbrian Water | PITY ME SEWAGE TREATMENT WORKS | 6NW800762 | 245/1274 | 245/1274 | 245/1274-03 | Storm tank at WwTW | NZ2630045940 | GB103024077622 | Blackdene Burn to confluence with Wear | BLACK DENE BURN |  |  | Commissioned in 2020 - full year data expected | 169.8972 | 55 | 100%
Northumbrian Water | PLAWSWORTH CSO MH1 | 6NW801233 | 245/E/0213 | 245/E/0213 |  | SO on sewer network | NZ2646447467 | GB103024077622 | Blackdene Burn to confluence with Wear | BLACK DENE BURN |  |  | Commissioned pre-2016 - full year data expected | 160.75 | 53 | 95.98% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | PLAWSWORTH SEWAGE TREATMENT WORKS | 6NW800763 | 245/A/0712 | 245/A/0712 | A2 | Storm tank at WwTW | NZ2646647468 | GB103024077622 | Blackdene Burn to confluence with Wear | Blackdene Burn |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | KELLOE SSO MANHOLE NO. 18 PLAYING FIELD | 6NW801419 | 243/0991 | 243/0991 |  | SO on sewer network | NZ3382037090 | GB103024077410 | Croxdale Beck from Source to Wear | COXHOE BECK, TRIBUTARY OF |  |  | Commissioned pre-2016 - full year data expected | 2.5 | 6 | 95.97%
Northumbrian Water | POINT A DAMSIDE CSO CM022 | 6NW801127 | 225/1064 | 225/1064 |  | SO on sewer network | NZ2013386105 | GB103022077061 | Wansbeck from Font to Bothal Burn | COTTING BURN |  |  | Commissioned pre-2016 - full year data expected | 161.5 | 30 | 97.39%
Northumbrian Water | THE KYLINS COMBINED SEWER OVERFLOW | 6NW800272 | 225/1065 | 225/1065 |  | SO on sewer network | NZ2002084980 | GB103022077061 | Wansbeck from Font to Bothal Burn | CHURCH BURN |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | POINT PLEASANT PUMPING STATION | 6NW800579 | 235/1691 | 235/1691 | 235/1691-01 | Storm discharge at pumping station | NZ3172066080 | GB510302310200 | TYNE | TYNE |  |  | Commissioned in 2020 - full year data expected | 7.8631 | 7 | 92.33%
Northumbrian Water | PONT BUNGALOWS | 6NW800978 | 234/1141 | 234/1141 |  | SO on sewer network | NZ1224752377 | GB103023074780 | Pont Burn Catchment (trib of Derwent) | PONT BURN (RIVER DERWENT) |  |  | Commissioned pre-2016 - full year data expected | 1.25 | 2 | 97.09%
Northumbrian Water | PONT LANE A CSO | 6NW800239 | 234/1054 | 234/1054 |  | SO on sewer network | NZ1250652428 | GB103023074780 | Pont Burn Catchment (trib of Derwent) | PONT BURN |  |  | Commissioned pre-2016 - full year data expected | 71.75 | 24 | 99.99%
Northumbrian Water | PONT B CSO | 6NW800979 | 234/1055 | 234/1055 |  | SO on sewer network | NZ1251052520 | GB103023074780 | Pont Burn Catchment (trib of Derwent) | TRIBUTARY PONT BURN |  |  | Commissioned pre-2016 - full year data expected | 194 | 42 | 97.97%
Northumbrian Water | PORT CLARENCE WEST PS OUTFALL | 6NW800649 | QR.25/04/1542 | QR.25/04/1542 | S1 | Storm discharge at pumping station | NZ4945021650 | GB510302509900 | TEES | RIVER TEES (SALINE ESTUARY) |  |  | Commissioned in 2020 - full year data expected | 58.1489 | 18 | 100%
Northumbrian Water | PORTRACK SEWAGE TREATMENT WORKS CSO INLET | 6NW800189 | 25/04/1657 | 25/04/1657 | 25/04/1657-02 | Inlet SO at WwTW | NZ4703019380 | 10 | #N/A | RIVER TEES (SALINE ESTUARY) |  |  | Commissioned in 2020 - full year data expected | 44.4822 | 35 | 87.28% | Comms failure / issue | Resolved - Feburary
Northumbrian Water | PORTRACK SEWAGE TREATMENT WORKS Storm Tank | 6NW800796 | 25/04/1657 | 25/04/1657 | 25/04/1657-01 | Storm tank at WwTW | NZ4703019380 | 10 | #N/A | RIVER TEES (SALINE ESTUARY) |  |  | Commissioned in 2020 - full year data expected | 534.4442 | 61 | 100%
Northumbrian Water | POTTER STREET PUMPING STATION | 6NW800587 | 235/1688 | 235/1688 | 235/1688-01 | Storm discharge at pumping station | NZ3209066110 | GB510302310200 | TYNE | TYNE SALINE ESTUARY |  |  | Commissioned in 2020 - full year data expected | 3.7553 | 2 | 100%
Northumbrian Water | POTTERY LANE PS | 6NW800183 | 245/1171 | 245/1171 | 245/1171-01 | Storm discharge at pumping station | NZ3538757274 | GB510302402900 | WEAR | WEAR ESTUARY |  |  | Commissioned in 2020 - full year data expected | 182.0675 | 26 | 100%
Northumbrian Water | POWBURN SEWAGE TREATMENT WORKS | 6NW800689 | 210/1295 | 210/1295 | 210/1295-02 | Storm tank at WwTW | NU0620416547 | GB102021073041 | Till from Linhope Burn to Roddam Burn | THE POW BURN (RIVER TILL) |  |  | Commissioned in 2020 - full year data expected | 1970.67 | 126 | 100%
Northumbrian Water | PRIESTLAND CLOSE CSO | 6NW800894 | 233/1256 | 233/1256 |  | SO on sewer network | NY9335063440 | GB103023075801 | Tyne from Watersmeet to Tidal Limit | HALGUT BURN |  |  | Commissioned pre-2016 - full year data expected | 4 | 1 | 99.98%
Northumbrian Water | PRIESTLEY CRESCENT CSO | 6NW800401 | 245/1386 | 245/1386 |  | SO on sewer network | NZ3899757745 | GB510302402900 | WEAR | WEAR ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 46.25 | 36 | 99.47%
Northumbrian Water | PRINCE CONSORT ROAD PUMPING STATION | 6NW801371 | 235/1657 | 235/1657 | 235/1657-01 | Storm discharge at pumping station | NZ3007064910 | GB510302310200 | TYNE | TYNE SALINE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 253.5 | 46 | 99.52%
Northumbrian Water | PRINCESS ANNE PARK CSO | 6NW801366 | 245/1334 | 245/1334 |  | SO on sewer network | NZ3038854530 | 9 | #N/A | OXCLOSE BURN (BIDDICK BURN) |  |  | Commissioned pre-2016 - full year data expected | 6.4333 | 7 | 97.42%
Northumbrian Water | PRIORY ROAD CSO | 6NW801567 | 254/1862 | 254/1862 |  | SO on sewer network | NZ4707817717 | GB510302509900 | TEES | OLD RIVER TEES |  |  | Commissioned pre-2016 - full year data expected | 78 | 33 | 99.86%
Northumbrian Water | PRISSICK SSO | 6NW801581 | QR.25/04/1575 | QR.25/04/1575 |  | SO on sewer network | NZ5151917090 | GB103025072210 | Marton West Beck Catchment (trib of Tidal Tees) | ORMESBY BECK |  |  | Commissioned pre-2016 - full year data expected | 31.75 | 5 | 97.86%
Northumbrian Water | PRUDHOE CSO 4 | 6NW800944 | 233/G/0117 | 233/G/0117 |  | SO on sewer network | NZ0848962625 | GB103023075801 | Tyne from Watersmeet to Tidal Limit | OTTER BURN |  |  | Commissioned pre-2016 - full year data expected | 5.6333 | 15 | 99.92%
Northumbrian Water | PRUDHOE PUMPING STATION | 6NW800504 | 233/0974 | 233/0974 | A1 | Storm discharge at pumping station | NZ1030064470 | GB103023075801 | Tyne from Watersmeet to Tidal Limit | TYNE |  |  | Commissioned pre-2016 - full year data expected | 62.75 | 9 | 92.49%
Northumbrian Water | STOCKTON RD & QUARRY HEADS LN CSOS | 6NW801264 | 245/E/0409 | 245/E/0409 |  | SO on sewer network | NZ2750041700 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | WEAR |  |  | Commissioned pre-2016 - full year data expected | 1.5 | 5 | 84.32% | Comms failure / issue | Resolved - March
Northumbrian Water | QUARRY LANE SSO | 6NW800954 | 242/D/0075 | 242/D/0075 |  | SO on sewer network | NZ1012025590 | GB103024072690 | Gaunless from Source to Hummer Beck | GREWBURN BECK |  |  | Commissioned pre-2016 - full year data expected | 20 | 8 | 99.99%
Northumbrian Water | QUARRY PLANTATION (ABOVE CLIFTON GARDENS) | 6NW800413 | Not on public register | EPRNB3990VN |  | SO on sewer network | NZ4286715217 | GB103025072595 | Tees from Skerne to Tidal Limit | River Tees |  |  | Commissioned in 2019 - full year data expected | 69.9333 | 28 | 100%
Northumbrian Water | QUAYSIDE (HILLGATE STREET CSO) | 6NW801213 | EPRBP3721GX | EPRBP3721GX |  | SO on sewer network | NZ2542263774 | 8 | #N/A | RIVER TYNE |  |  | Commissioned pre-2016 - full year data expected | 1.25 | 2 | 99.99%
Northumbrian Water | QUAYSIDE/ST LAWRENCE ROAD CSO | 6NW801247 | 235/1766 | 235/1766 |  | SO on sewer network | NZ2653864027 | GB510302310200 | TYNE | RIVER TYNE SALINE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 100%
Northumbrian Water | QUEBEC PUMPING STATION | 6NW800513 | 244/A/0456 | 244/A/0456 | 244/A/0456-02 | Storm discharge at pumping station | NZ1824043930 | GB103024077551 | Browney from Smallhope Burn Deerness confl | HAMSTEELS BECK |  |  | Commissioned in 2020 - full year data expected | 313.2533 | 38 | 99.66%
Northumbrian Water | QUEEN ALEXANDRA PS | 6NW800610 | 245/0928 | 245/0928 | 245/0928-01 | Storm discharge at pumping station | NZ3817057880 | 9 | #N/A | WEAR (TIDAL) |  |  | Commissioned in 2020 - full year data expected | 135.2797 | 41 | 99.94%
Northumbrian Water | QUEEN STREET ALLOTTMENTS CSO | 6NW801599 | 25/04/1777 | 25/04/1777 |  | SO on sewer network | NZ5717020090 | GB103025072320 | Tees Estuary (S Bank) | UNNAMED TRIB OF DABHOLME BECK |  |  | Commissioned pre-2016 - full year data expected | 3.75 | 5 | 99.99%
Northumbrian Water | QUEENS GARDENS CSO | 6NW800826 | 210/1007 | 210/1007 |  | SO on sewer network | NT9962352760 | 3 | #N/A | TWEED ESTUARY |  | Spittal | Commissioned pre-2016 - full year data expected | 139.3667 | 57 | 99.73% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | QUEENSPORT CLOSE CSO | 6NW801560 | 254/1829 | 254/1829 |  | SO on sewer network | NZ4570020200 | GB103025072550 | Lustrum Beck Catchment (trib of Tees) | LUSTRUM BECK |  |  | Commissioned pre-2016 - full year data expected | 84.5 | 25 | 99.98%
Northumbrian Water | QUEENSWAY CSO | 6NW800950 | 234/1134 | 234/1134 |  | SO on sewer network | NZ0910052300 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | BACKSTONE BURN |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.96%
Northumbrian Water | RGIL LOCKHAUGH RD & SHRBURN PRK CSO | 6NW801031 | 234/1130 | 234/1130 |  | SO on sewer network | NZ1691359126 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | TRIB RIVER DERWENT |  |  | Commissioned pre-2016 - full year data expected | 18.5 | 9 | 84.14% | Sensor failure / issue | Resolved - December
Northumbrian Water | REAR OF RABY ROAD STORM SEWAGE OVER | 6NW800924 | 252/1123 | 252/1123 |  | SO on sewer network | NZ0460016730 | GB103025072512 | Tees from Percy Beck to River Greta | TEES |  |  | Commissioned pre-2016 - full year data expected | 0.25 | 1 | 83.56% | Comms failure / issue | Scheduled
Northumbrian Water | RAF BOULMER SEWAGE PUMPING STATION | 6NW800467 | 221/1036 | 221/1036 | 221/1036-01 | Storm discharge at pumping station | NU2680015660 | GB650301500001 | Northumberland South | NORTH SEA |  |  | Commissioned in 2020 - full year data expected | 699.9836 | 56 | 100%
Northumbrian Water | RAILWAY GARDENS CSO DER047 | 6NW801026 | 235/1930 | 235/1930 |  | SO on sewer network | NZ1687452291 | GB103023075670 | Team from Source to Tyne | KYO BURN (RIVER TEAM) |  |  | Commissioned pre-2016 - full year data expected | 12.25 | 17 | 98.03%
Northumbrian Water | RAILWAY LINE CSO | 6NW801443 | 243/1014 | 243/1014 |  | SO on sewer network | NZ3408536027 | GB103024077410 | Croxdale Beck from Source to Wear | COXHOE BECK |  |  | Commissioned pre-2016 - full year data expected | 103.4333 | 48 | 98.56%
Northumbrian Water | RAILWAY SREET CSO | 6NW801024 | 244/0938 | 244/0938 |  | SO on sewer network | NZ1664347223 | GB103024077330 | Smallhope Burn from Source to Browney, Stocke | SMALLHOPE BURN |  |  | Commissioned pre-2016 - full year data expected | 165 | 38 | 98.86% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | RAILWAY STATION STOCKSFIELD CSO | 6NW800931 | 233/D/0068 | 233/D/0068 |  | SO on sewer network | NZ0547961386 | GB103023075640 | Stocksfield Burn Catchment (trib of Tyne) | STOCKSFIELD BURN (RIVER TYNE) |  |  | Commissioned pre-2016 - full year data expected | 28.75 | 18 | 96.5%
Northumbrian Water | RAILWAY STREET | 6NW801625 | 210/1350 | 210/1350 |  | SO on sewer network | NT9937153235 | GB510202110000 | TWEED | RIVER TWEED (SALINE ESTUARY) |  | Spittal | Commissioned pre-2016 - full year data expected | 4.1 | 12 | 99.76%
Northumbrian Water | RAMSHAW PS | 6NW800241 | 242/1007 | 242/1007 | 242/1007-01 | Storm discharge at pumping station | NZ1513025980 | GB103024072690 | Gaunless from Source to Hummer Beck | GORDON BECK (RIVER GAUNLESS) |  |  | Commissioned in 2017 - full year data expected | 4 | 6 | 93.43%
Northumbrian Water | RAMSHAW SEWAGE TREATMENT WORKS | 6NW800153 | 242/1071 | 242/1071 | A3 | Inlet SO at WwTW | NZ1549526058 | GB103024072690 | Gaunless from Source to Hummer Beck | GAUNLESS |  |  | Commissioned in 2020 - full year data expected | 106.8417 | 39 | 88.43% | Installation set-up/design issue | Resolved - October
Northumbrian Water | RAMSHAW SEWAGE TREATMENT WORKS Storm Tank | 6NW800731 | 242/1071 | 242/1071 | A2 | Storm tank at WwTW | NZ1549526058 | GB103024072690 | Gaunless from Source to Hummer Beck | GAUNLESS |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | RAVENSCROFT AVE CSO | 6NW801409 | 254/1922 | 254/1922 |  | SO on sewer network | NZ4952017770 | GB103025072210 | Marton West Beck Catchment (trib of Tidal Tees) | MARTON WEST BECK |  |  | Commissioned pre-2016 - full year data expected | 10.25 | 3 | 99.99%
Northumbrian Water | RAVENSDOWNE BARRACKS SPS | 6NW800458 | 210/1251 | 210/1251 | A1 | Storm discharge at pumping station | NU0036052510 | GB510202110000 | TWEED | RIVER TWEED (SALINE ESTUARY) |  | Spittal | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
Northumbrian Water | DAVEY LAMP PH CSO BURNETT CRESCENT | 6NW801624 | 243/0990 | 243/0990 |  | SO on sewer network | NZ3426036230 | GB103024077410 | Croxdale Beck from Source to Wear | COXHOE BECK |  |  | Commissioned pre-2016 - full year data expected | 15 | 18 | 98.63%
Northumbrian Water | REAR 3 ERNEST STREET CSO | 6NW801465 | EPRAB3390WN | EPRAB3390WN |  | SO on sewer network | NZ3543562359 | GB103023075690 | Don from Source to Tidal Limit | RIVER DON |  |  | Commissioned pre-2016 - full year data expected | 2.5 | 2 | 99.99%
Northumbrian Water | REAR 39 CUTLERS HALL ROAD | 6NW801632 | 234/1133 | 234/1133 |  | SO on sewer network | NZ0895152310 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | BACKSTONE BURN |  |  | Commissioned pre-2016 - full year data expected | 0.5 | 2 | 96.68%
Northumbrian Water | REAR OF 92 & 94 CHARLES STREET CSO | 6NW800373 | EPRAB3290DW | EPRAB3290DW |  | SO on sewer network | NZ3543562358 | GB103023075690 | Don from Source to Tidal Limit | RIVER DON |  |  | Commissioned in 2017 - full year data expected | 0 | 0 | 99.67%
Northumbrian Water | JARROW HEDWORTH CSO 23 CHARLES STREET | 6NW801454 | EPRAB3291RT | EPRAB3291RT |  | SO on sewer network | NZ3543562359 | GB103023075690 | Don from Source to Tidal Limit | RIVER DON |  |  | Commissioned pre-2016 - full year data expected | 2.5 | 4 | 99.99%
Northumbrian Water | JARROW HEDWORTH CSO 20 ARNOLD STREET | 6NW801453 | EPRAB3290EA | EPRAB3290EA |  | SO on sewer network | NZ3543562359 | GB103023075690 | Don from Source to Tidal Limit | RIVER DON |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.83%
Northumbrian Water | REAR FORSTER ST/EASSON ROAD CSO | 6NW801298 | EPRBB3699VN | EPRBB3699VN |  | SO on sewer network | NZ2918014935 | GB103025072596 | Skerne from Demons Beck to Tees | RIVER SKERNE |  |  | Commissioned pre-2016 - full year data expected | 0.25 | 1 | 98.37%
Northumbrian Water | REAR OF THIRD STREET CSO | 6NW801552 | 255/1211 | 255/1211 |  | SO on sewer network | NZ4466041300 | 367 | #N/A | BLACKHILLS GILL |  |  | Commissioned pre-2016 - full year data expected | 0.5 | 1 | 99.99%
Northumbrian Water | REAR OF WELL HOUSE FARM CSO | 6NW801442 | NPSWQD009688 | NPSWQD009688 |  | SO on sewer network | NZ3412617086 | GB103025072596 | Skerne from Demons Beck to Tees | CARCUT BECK |  |  | Commissioned pre-2016 - full year data expected | 7 | 13 | 99.73%
Northumbrian Water | REAR ST MICHAELS CSO | 6NW801656 | 245/1316 | 245/1316 |  | SO on sewer network | NZ3296449620 | GB103024077580 | Lumley Park Burn from Source to Herrington Burn | RED BURN |  |  | Commissioned pre-2016 - full year data expected | 2.5 | 6 | 99.97%
Northumbrian Water | RECTORY COTTAGE CSO | 6NW801146 | 243/0971 | 243/0971 |  | SO on sewer network | NZ2250737849 | GB103024077420 | Brancepeth Beck from Source to Wear | BRANCEPETH BECK, TRIBUTARY OF |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | BAMBURGH SEWAGE PUMPING STATION RED BARNS | 6NW800463 | 221/1069 | 221/1069 | 221/1069-01 | Storm discharge at pumping station | NU1973035020 | GB650301440000 | Northumberland North | NORTH SEA |  | Bamburgh Castle | Commissioned in 2018 - full year data expected | 25.3922 | 10 | 100%
Northumbrian Water | RED ROW SEWAGE PUMPING STATION | 6NW800533 | 224/A/0616 | 224/A/0616 | A1 | Storm discharge at pumping station | NZ2541098908 | GB103022076521 | Chevington Burn/Steads Burn from Source to Tidal Limit | CHEVINGTON BURN |  |  | Commissioned in 2020 - full year data expected | 196.725 | 21 | 100%
Northumbrian Water | REDBURN SEWAGE PUMPING STATION | 6NW800488 | 232/1170 | 232/1170 | 232/1170-02 | Storm discharge at pumping station | NY7704764478 | GB103023075532 | South Tyne from Tipalt Burn to Allen | RED BURN |  |  | Commissioned in 2020 - full year data expected | 5.6111 | 37 | 99.95%
Northumbrian Water | REDWELL SEAGE PUMPING STATION | 6NW800613 | 235/1588 | 235/1588 | 235/1588-02 | Storm discharge at pumping station | NZ3975065880 | GB650301500002 | Tyne and Wear | NORTH SEA |  | Marsden | Commissioned pre-2016 - full year data expected | 61.8333 | 19 | 96.49%
Northumbrian Water | REDWORTH SEWAGE PUMPING STATION | 6NW800529 | 253/D/0204 | 253/D/0204 | A1 | Storm discharge at pumping station | NZ2410523582 | GB103025072400 | Woodham Burn from Source to Rushyford beck | RED HOUSE BECK, TRIBUTARY OF |  |  | Commissioned in 2019 - full year data expected | 77.9447 | 26 | 100%
Northumbrian Water | RENNINGTON PUMPING STATION | 6NW800464 | 221/1066 | 221/1066 | 221/1066-01 | Storm discharge at pumping station | NU2134018450 | GB103022076360 | Rennington Burn from Source to N Sea | RENNINGTON BURN |  |  | Commissioned in 2020 - full year data expected | 134.4878 | 28 | 99.65%
Northumbrian Water | RENNYS LANE PUMPING STATION | 6NW800571 | 245/A/0464 | 245/A/0464 | 245/A/0464-02 | Storm discharge at pumping station | NZ3107842600 | GB103024077540 | Pittington Beck from Coalford to Old Durham Beck | PITTINGTON BECK |  |  | Commissioned in 2020 - full year data expected | 23.9742 | 14 | 100%
Northumbrian Water | REYROLLE SEWER (SOUTH) CSO | 6NW800356 | 235/1186 | 235/1186 |  | SO on sewer network | NZ3001764352 | GB510302310200 | TYNE | RIVER TYNE |  |  | Commissioned in 2018 - full year data expected | 171 | 65 | 99.35%
Northumbrian Water | RICHARD STREET PUMPING STATION | 6NW800672 | 256/1075 | 256/1075 | 256/1075-01 | Storm discharge at pumping station | NZ6189019360 | GB103025071970 | Skelton Beck Catch (Saltburn) trib of North Sea | HOLME BECK & NEW HILL GILL |  |  | Commissioned in 2016 - full year data expected | 0.75 | 3 | 99.99%
Northumbrian Water | RIDING DENE CSO | 6NW800938 | 233/G/0178 | 233/G/0178 |  | SO on sewer network | NZ0732562359 | GB103023075801 | Tyne from Watersmeet to Tidal Limit | TRIBUTARY OF TYNE |  |  | Commissioned pre-2016 - full year data expected | 62.1264 | 24 | 90.2%
Northumbrian Water | RIDING MILL VILLAGE SPS | 6NW800498 | 233/1040 | 233/1040 | A1 | Storm discharge at pumping station | NZ0190061480 | GB103023075650 | March Burn Catchment (trib of Tyne) | RIDING MILL BURN |  |  | Commissioned in 2020 - full year data expected | 196.4994 | 39 | 100%
Northumbrian Water | RIDLEY MILL ROAD CSO | 6NW800929 | 233/1254 | 233/1254 |  | SO on sewer network | NZ0573060260 | GB103023075640 | Stocksfield Burn Catchment (trib of Tyne) | BAT BURN |  |  | Commissioned pre-2016 - full year data expected | 107.5 | 19 | 99.91%
Northumbrian Water | RIDLEY STREET SPS | 6NW800582 | 226/1175 | 226/1175 | A1 | Storm discharge at pumping station | NZ3199081540 | 5 | #N/A | RIVER BLYTH(SALINE ESTUARY) |  |  | Commissioned in 2020 - full year data expected | 7.75 | 4 | 100%
Northumbrian Water | VINOVIUM SSO NO A32 RIVER WALK WV 12 | 6NW801060 | 242/1062 | 242/1062 |  | SO on sewer network | NZ1858026500 | GB103024072690 | Gaunless from Source to Hummer Beck | GAUNLESS |  |  | Commissioned pre-2016 - full year data expected | 3.25 | 6 | 99.99%
Northumbrian Water | RIVERSDALE ROAD CSO | 6NW800309 | 235/1365 | 235/1365 |  | SO on sewer network | NZ2466763084 | GB510302310200 | TYNE | RIVER TYNE |  |  | Commissioned in 2018 - full year data expected | 3.5 | 9 | 100%
Northumbrian Water | RIVERSIDE (BUTTS CRESCENT) CSO | 6NW800913 | 241/1091 | 241/1091 |  | SO on sewer network | NY9957039040 | GB103024077461 | Wear from Middlehope Burn to Houselop Beck | RIVER WEAR |  |  | Commissioned pre-2016 - full year data expected | 37.25 | 28 | 99.98%
Northumbrian Water | RIVERSIDE CSO | 6NW801131 | 242/1043 | 242/1043 |  | SO on sewer network | NZ2174028658 | GB103024077461 | Wear from Middlehope Burn to Houselop Beck | COUNDON BURN |  |  | Commissioned pre-2016 - full year data expected | 706.75 | 79 | 99.7% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | RIVERSIDEWAY CSO | 6NW800270 | EPRCB3191VZ | EPRCB3191VZ |  | SO on sewer network | NZ2047663110 | 8 | #N/A | RIVER DERWENT |  |  | Commissioned in 2018 - full year data expected | 466.085 | 48 | 100%
Northumbrian Water | ROKER STORM SEWAGE OVERFLOW | 6NW800409 | 245/1109 | 245/1109 |  | SO on sewer network | NZ4073059220 | GB650301500002 | Tyne and Wear | NORTH SEA |  | Roker (Whitburn South) | Commissioned in 2018 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | ROMALDKIRK SEWAGE DISPOSAL WORKS CSO INLET | 6NW800142 | 25/01/0912 | 25/01/0912 | 25/01/0912-04 | Inlet SO at WwTW | NZ0020022600 | GB103025072511 | Tees from Maize Beck to Percy Beck | RIVER TEES |  |  | June 2021 | 0.65444 | 3 | 99.44%
Northumbrian Water | ROMALDKIRK SEWAGE DISPOSAL WORKS Storm Tank | 6NW800711 | 25/01/0912 | 25/01/0912 | 25/01/0912-03 | Storm tank at WwTW | NZ0020022600 | GB103025072511 | Tees from Maize Beck to Percy Beck | RIVER TEES |  |  | Commissioned in 2020 - full year data expected | 69.0339 | 23 | 100%
Northumbrian Water | ROMAN ROAD CSO | 6NW801432 | 235/1703 | 235/1703 |  | SO on sewer network | NZ3334563408 | GB103023075690 | Don from Source to Tidal Limit | RIVER DON |  |  | Commissioned pre-2016 - full year data expected | 266.25 | 43 | 98.19%
Northumbrian Water | ROOKHOPE STW | 6NW800138 | 241/1145 | 241/1145 | A2 | Inlet SO at WwTW | NY9429041830 | GB103024077530 | Rookhope Burn from Source to Wear | ROOKHOPE BURN |  |  | Commissioned in 2020 - full year data expected | 792.2364 | 83 | 96.53%
Northumbrian Water | ROPERY LANE/EARDULPH AVE CSO | 6NW801278 | 245/1088 | 245/1088 |  | SO on sewer network | NZ2836950977 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | WEAR |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | ROSE COTTAGE PUMPING STATION | 6NW800930 | 233/1220 | 233/1220 | 233/1220-01 | Storm discharge at pumping station | NZ0532061760 | GB103023075640 | Stocksfield Burn Catchment (trib of Tyne) | STOCKSFIELD BURN |  |  | Commissioned pre-2016 - full year data expected | 257 | 39 | 65.18% | Comms failure / issue | Resolved - October
Northumbrian Water | ROSE CRESCENT CSO | 6NW801365 | 245/1096 | 245/1096 |  | SO on sewer network | NZ3094050890 | GB103024077570 | Lumley Park Burn from Herrington Burn to R Wear | LUMLEY PARK BURN |  |  | Commissioned pre-2016 - full year data expected | 1 | 1 | 99.99%
Northumbrian Water | ROSE STREET CSO | 6NW800307 | 235/1917 | 235/1917 |  | SO on sewer network | NZ2427162857 | GB510302310200 | TYNE | RIVER TYNE |  |  | Commissioned in 2019 - full year data expected | 27.6608 | 30 | 100%
Northumbrian Water | ROSE TERRACE CSO | 6NW800911 | 241/1089 | 241/1089 |  | SO on sewer network | NY9917239203 | GB103024077461 | Wear from Middlehope Burn to Houselop Beck | RIVER WEAR |  |  | Commissioned pre-2016 - full year data expected | 1.75 | 4 | 96.36%
Northumbrian Water | ROSELEIGH CSO | 6NW800969 | 233/1055 | 233/1055 |  | SO on sewer network | NZ1167164640 | 8 | #N/A | RIVER TYNE VIA SURFACE WTR SWR |  |  | Commissioned pre-2016 - full year data expected | 0.25 | 1 | 84.45% | Comms failure / issue | Resolved - November
Northumbrian Water | ROTHBURY SEWAGE TREATMENT WORKS | 6NW800690 | 223/0820 | 223/0820 | A2 | Inlet SO at WwTW | NU0718001062 | GB103022076692 | Coquet from Holystone Burn to Forest Burn | COQUET |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | CSO WV79 ROUGH LEA LANE | 6NW800261 | 243/0909 | 243/0909 |  | SO on sewer network | NZ1936133626 | GB103024077464 | Wear from Gaunless to Browney | UNNAMED BECK TRIB RVR WEAR |  |  | Commissioned in 2016 - full year data expected | 5.25 | 13 | 99.99%
Northumbrian Water | ROWAN DRIVE CSO (DU 52) | 6NW801310 | 245/1326 | 245/1326 |  | SO on sewer network | NZ2842045860 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | REDHOUSE GILL, TRIBUTARY OF |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | ROWLANDSON TERRACE CSO | 6NW801337 | 253/1080 | 253/1080 |  | SO on sewer network | NZ3042931758 | GB103025072520 | Carrs from Source to Skerne | CARRS TRIBUTARY |  |  | Commissioned pre-2016 - full year data expected | 7.25 | 16 | 92.42%
Northumbrian Water | RUSHYFORD SEWAGE PUMPING STATION, A | 6NW801302 | 253/0600 | 253/0600 | 253/0600-03 | Storm discharge at pumping station | NZ2838028690 | GB103025072450 | Rushyford Beck from Source to Woodham Burn | RUSHYFORD BECK |  |  | Commissioned pre-2016 - full year data expected | 605.25 | 44 | 99.1%
Northumbrian Water | RUSSEL PLACE CSO | 6NW801109 | 243/1007 | 243/1007 |  | SO on sewer network | NZ2069634696 | GB103024077464 | Wear from Gaunless to Browney | WEAR TRIBUTARY |  |  | Commissioned pre-2016 - full year data expected | 117.25 | 27 | 99.99%
Northumbrian Water | RUTLAND STREET/LEEHOLME ROAD CSO | 6NW801174 | 253/1260 | 253/1260 |  | SO on sewer network | NZ2573030190 | GB103025072450 | Rushyford Beck from Source to Woodham Burn | RUSHYFORD BECK TRIBUTARY |  |  | Commissioned pre-2016 - full year data expected | 0.5 | 2 | 99.99%
Northumbrian Water | RYHOPE SSO | 6NW800411 | 255/1200 | 255/1200 |  | SO on sewer network | NZ4170053130 | GB650301500002 | Tyne and Wear | NORTH SEA |  |  | Commissioned in 2020 - full year data expected | 144.9494 | 48 | 100%
Northumbrian Water | SACRISTON SEWAGE TREATMENT WORKS | 6NW800758 | 245/1254 | 245/1254 | 245/1254-03 | Storm tank at WwTW | NZ2462047880 | GB103024077623 | South Burn to confluence with Wear | SOUTH BURN |  |  | Commissioned in 2020 - full year data expected | 756.4917 | 57 | 99.97%
Northumbrian Water | SADBERGE SEWAGE PUMPING STATION | 6NW800592 | 25/04/1749 | 25/04/1749 | 25/04/1749-01 | Storm discharge at pumping station | NZ3423015970 | GB103025072160 | Neasham Stell Catchment (trib of Tees) | BUMPER HA\LL BECK |  |  | Commissioned pre-2016 - full year data expected | 2.25 | 6 | 88.2% | Comms failure / issue | Resolved - March
Northumbrian Water | SADBERGE SEWAGE TREATMENT WORKS | 6NW800180 | 25/03/1235 | 25/03/1235 | 25/03/1235-02 | Inlet SO at WwTW | NZ3403017320 | GB103025072596 | Skerne from Demons Beck to Tees | CARCUT BECK (SKERNE CATCHMENT) |  |  | Commissioned in 2020 - full year data expected | 13.9122 | 6 | 91.77%
Northumbrian Water | SALISBURY PS | 6NW800552 | 245/1047 | Permit Anomaly - EO permit 245/1047 | To be permitted for storm | Storm discharge at pumping station | NZ2837045893 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | Redhouse Gill |  |  | Commissioned in 2020 - full year data expected | 9.0142 | 7 | 100%
Northumbrian Water | SALTERS LANE CSO | 6NW800321 | 235/1895 | 235/1895 |  | SO on sewer network | NZ2560468471 | GB103023075780 | Ouse Burn from Source to Tyne | OUSE BURN |  |  | Commissioned in 2018 - full year data expected | 401.6722 | 41 | 100%
Northumbrian Water | SALTMEADOWS PUMPING STATION | 6NW800536 | 235/1195 | 235/1195 | 235/1195-01 | Storm discharge at pumping station | NZ2616064000 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | Commissioned in 2020 - full year data expected | 15.7664 | 4 | 99.98%
Northumbrian Water | QUAY WALL SPS SANDGATE CSO | 6NW800210 | 210/0935 | 210/0935 |  | SO on sewer network | NT9979852582 | GB510202110000 | TWEED | RIVER TWEED ESTUARY |  | Spittal | Commissioned pre-2016 - full year data expected | 223.6333 | 65 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | SANDS SYPHON SSO | 6NW801274 | 245/0906 | 245/0906 |  | SO on sewer network | NZ2793243111 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | RIVER WEAR |  |  | Commissioned pre-2016 - full year data expected | #N/A | #N/A | 0% | Comms failure / issue | Scheduled | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | SATLEY STW | 6NW800148 | 244/A/0494 | 244/A/0494 |  | Inlet SO at WwTW | NZ1202143854 | GB103024077310 | Browney from Source to Pan Burn | Steeley Burn |  |  | Commissioned in 2020 - full year data expected | 15.9561 | 25 | 95.8%
Northumbrian Water | SCORERS LANE CSO | 6NW801340 | 245/1307 | 245/1307 |  | SO on sewer network | NZ2955049740 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | BROUGHS GILL |  |  | Commissioned pre-2016 - full year data expected | 3.75 | 3 | 99.99%
Northumbrian Water | SCOTCH ISLE FARM CSO | 6NW800939 | 241/1120 | 241/1120 |  | SO on sewer network | NZ0898536517 | GB103024077461 | Wear from Middlehope Burn to Houselop Beck | UNNAMED TRIB OF RIVER WEAR |  |  | Commissioned pre-2016 - full year data expected | #N/A | #N/A | 0% | Comms failure / issue | Scheduled
Northumbrian Water | SCOTS GAP STW | 6NW800714 | 225/A/0871 | 225/A/0871 |  | Storm tank at WwTW | NZ0421886073 | GB103022076990 | Wansbeck from Ray Burn to Hart Burn | Middleton Burn |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | SCOTSWOOD BRIDGE CSO | 6NW800268 | 235/1669 | 235/1669 |  | SO on sewer network | NZ2000963684 | GB510302310200 | TYNE | TYNE SALINE ESTUARY |  |  | Commissioned in 2017 - full year data expected | 0.9 | 1 | 99.95%
Northumbrian Water | SCOTSWOOD NO1 SPS | 6NW800522 | 235/1673 | 235/1673 | A1 | Storm discharge at pumping station | NZ2124063430 | 8 | #N/A | TYNE SALINE ESTUARY |  |  | Commissioned in 2020 - full year data expected | 216.7892 | 17 | 100%
Northumbrian Water | SCOTSWOOD ROAD/DENTON BURN PS | 6NW800517 | 235/1668 | 235/1668 | 235/1668-01 | Storm discharge at pumping station | NZ1972063930 | GB510302310200 | TYNE | TYNE SALINE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 47.5 | 24 | 99.97%
Northumbrian Water | SCOTSWOOD ROAD PUMPING STATION NO 4 | 6NW800516 | 235/1667 | 235/1667 | 235/1667-01 | Storm discharge at pumping station | NZ1942064070 | GB510302310200 | TYNE | TYNE SALINE ESTUARY |  |  | Commissioned in 2020 - full year data expected | 127.5261 | 18 | 100%
Northumbrian Water | SCOTSWOOD ROAD PUMPING STATION NO 2 | 6NW800519 | 235/1670 | 235/1670 | 235/1670-01 | Storm discharge at pumping station | NZ2045063500 | GB510302310200 | TYNE | RIVER TYNE |  |  | Commissioned in 2016 - full year data expected | 0 | 0 | 96.71%
Northumbrian Water | SCOUT HOUSE FARM 1 CSO | 6NW800290 | 244/0998 | 244/0998 |  | SO on sewer network | NZ2273042050 | GB103024077280 | Deerness from Hedleyhope Burn to Browney | RIVER DEERNESS |  |  | Commissioned pre-2016 - full year data expected | 245.75 | 24 | 92.61%
Northumbrian Water | SCOUT HOUSE FARM 2 CSO | 6NW801149 | 244/1005 | 244/1005 |  | SO on sewer network | NZ2289441947 | GB103024077280 | Deerness from Hedleyhope Burn to Browney | RIVER DEERNESS |  |  | Commissioned pre-2016 - full year data expected | 4.75 | 8 | 94.38%
Northumbrian Water | SCREMERSTON NO 1 SPS | 6NW800680 | 210/0880 | 210/0880 | A1 | Storm discharge at pumping station | NU0237049560 | GB650301440000 | Northumberland North | DOUPSTER BURN/NORTH SEA |  |  | Commissioned in 2020 - full year data expected | 86.6744 | 25 | 99.82%
Northumbrian Water | SCREMERSTON NO 2 SPS | 6NW800681 | EPRTB3996RM | EPRTB3996RM | A1 | Storm discharge at pumping station | NU0237049560 | GB650301440000 | Northumberland North | DOUPSTER BURN/NORTH SEA |  |  | Commissioned in 2020 - full year data expected | 866.7675 | 95 | 99.79%
Northumbrian Water | SEA ROAD CSO | 6NW800844 | EPRPP3227GJ | EPRPP3227GJ |  | SO on sewer network | NU0018151930 | GB510202110000 | TWEED | TWEED ESTUARY |  | Spittal | Commissioned pre-2016 - full year data expected | 0.2 | 1 | 100%
Northumbrian Water | SEA VIEW CSO | 6NW801354 | 224/0994 | 224/0994 |  | SO on sewer network | NZ2979191095 | 362 | #N/A | RIVER LYNE |  |  | Commissioned pre-2016 - full year data expected | 598.25 | 57 | 60.96% | Comms failure / issue | Resolved - September | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | SEA VIEW STORAGE TANK | 6NW800406 | 255/1178 | 255/1178 |  | SO on sewer network | NZ4030047850 | GB103025075970 | Dalton Beck to North Sea | DALTON BURN |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | SEABURN NORTH CSO | 6NW801515 | 245/1107 | 245/1107 |  | SO on sewer network | NZ4060060210 | GB650301500002 | Tyne and Wear | NORTH SEA |  | Seaburn (Whitburn North) | Commissioned pre-2016 - full year data expected | 0.63333 | 1 | 100%
Northumbrian Water | SEABURN SOUTH CSO | 6NW801514 | 245/1108 | 245/1108 |  | SO on sewer network | NZ4060060190 | GB650301500002 | Tyne and Wear | NORTH SEA |  | Seaburn (Whitburn North) | Commissioned pre-2016 - full year data expected | 0.46667 | 1 | 100%
Northumbrian Water | SEAHAM CSO NO 8 | 6NW801535 | 255/E/0620 | 255/E/0620 |  | SO on sewer network | NZ4210848831 | GB103025075970 | Dalton Beck to North Sea | SEATON BURN/ICE HOUSE DENE/DAW |  | Seaham Hall | Commissioned pre-2016 - full year data expected | 7.4333 | 22 | 99.99%
Northumbrian Water | SEAHAM ROAD CSO SU35 | 6NW801450 | 245/1363 | 245/1363 |  | SO on sewer network | NZ3481149956 | GB103024077580 | Lumley Park Burn from Source to Herrington Burn | HOUGHTON BURN |  |  | Commissioned pre-2016 - full year data expected | 109.75 | 48 | 99.73%
Northumbrian Water | SEAHAM SOUTH DOCK CSO 1302 | 6NW800417 | EPRYB3835AX | EPRYB3835AX |  | SO on sewer network | NZ4324449198 | GB650301500002 | Tyne and Wear | SEAHAM SOUTH DOCK (NORTH SEA) |  |  | Commissioned in 2017 - full year data expected | 0 | 0 | 100%
Northumbrian Water | SEAHAM SEWAGE TREATMENT WORKS | 6NW800188 | 255/1125 | 255/1125 | 255/1125-03 | Inlet SO at WwTW | NZ4529047170 | GB650301500002 | Tyne and Wear | NORTH SEA |  |  | Commissioned in 2020 - full year data expected | 864.1261 | 67 | 100%
Northumbrian Water | SEAMER PS | 6NW800646 | 254/0981 | 254/0981 | A | Storm discharge at pumping station | NZ4957009930 | GB103025071880 | Leven from Tame to River Tees | SEAMER STELL (LEVEN) |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | SEATON CAREW SEWAGE TREATMENT WORKS | 6NW800196 | 254/1966 | 254/1966 | 254/1966-05 | Inlet SO at WwTW | NZ5350030100 | GB650301500005 | Tees Coastal | NORTH SEA |  | Seaton Carew (North) | Commissioned in 2019 - full year data expected | 416.0294 | 94 | 100%
Northumbrian Water | SEAHAM URBAN DISTRICT COUNCIL SSO SEATON CSO 1 | 6NW801502 | 255/E/0645 | 255/E/0645 |  | SO on sewer network | NZ4100050400 | 367 | #N/A | SEATON BURN |  |  | Commissioned pre-2016 - full year data expected | 3.75 | 7 | 99.97%
Northumbrian Water | SEATON NORTH HOTEL CSO (WK013) | 6NW801323 | 225/1070 | 225/1070 |  | SO on sewer network | NZ2814686018 | GB103022077062 | Wansbeck from Bothal Burn to North Sea | ROWLINGTON BURN(R WANSBECK) |  |  | Commissioned pre-2016 - full year data expected | 210.75 | 57 | 99.85% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution
Northumbrian Water | SEATON SLUICE PS | 6NW800591 | 226/0946 | 226/0946 | A | Storm discharge at pumping station | NZ3398076990 | GB650301500002 | Tyne and Wear | NORTH SEA |  | Seaton Sluice | Commissioned in 2018 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | SEDGEFIELD SEWAGE TREATMENT WORKS | 6NW800785 | 254/1864 | 254/1864 | 254/1864-04 | Storm tank at WwTW | NZ3602027950 | GB103025072410 | Billingham Beck from Source to Bishopton Beck | SHOTTON BECK, TRIBUTARY OF |  |  | Commissioned in 2020 - full year data expected | 1201.0375 | 65 | 99.78%
Northumbrian Water | SEDGELETCH BRIDGE CSO | 6NW801408 | 245/1377 | 245/1377 |  | SO on sewer network | NZ3256050720 | GB103024077580 | Lumley Park Burn from Source to Herrington Burn | MOORS BURN |  |  | Commissioned pre-2016 - full year data expected | 43.5 | 22 | 99.99%
Northumbrian Water | SEDGELETCH STW CSO INLET | 6NW800176 | 245/1243 | 245/1243 | A3 | Inlet SO at WwTW | NZ3244050818 | GB103024077580 | Lumley Park Burn from Source to Herrington Burn | HERRINGTON BURN/MOORS BURN |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | SEDGELETCH STW Storm Tank | 6NW800780 | 245/1243 | 245/1243 | A2 | Storm tank at WwTW | NZ3244050818 | GB103024077580 | Lumley Park Burn from Source to Herrington Burn | HERRINGTON BURN/MOORS BURN |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | SEGHILL CSO | 6NW801318 | 226/F/0419 | 226/F/0419 |  | SO on sewer network | NZ2836774535 | GB103022076190 | Seaton Burn from Source to Tidal Limit | SEATON BURN |  |  | Commissioned pre-2016 - full year data expected | 14.4 | 42 | 100%
Northumbrian Water | SEYMOUR CRESCENT CSO | 6NW800410 | 254/1824 | 254/1824 |  | SO on sewer network | NZ4118413610 | GB103025072595 | Tees from Skerne to Tidal Limit | NELLY BURDON'S BECK |  |  | Commissioned in 2020 - full year data expected | 3.0753 | 11 | 99.99%
Northumbrian Water | SHARPNESS POINT PS | 6NW800605 | 235/1582 | 235/1582 | 235/1582-01 | Storm discharge at pumping station | NZ3718069940 | GB650301500002 | Tyne and Wear | NORTH SEA |  | Tynemouth Longsands South | Commissioned in 2019 - full year data expected | 13.2214 | 4 | 92.19%
Northumbrian Water | SHERATON CSO | 6NW801344 | 235/A/0509 | 235/A/0509 |  | SO on sewer network | NZ3060059900 | GB103023075690 | Don from Source to Tidal Limit | DON |  |  | Commissioned pre-2016 - full year data expected | 2.5 | 1 | 97.69%
Northumbrian Water | SHERBURN SSO MANHOLE NO 32 | 6NW801421 | 245/E/0511 | 245/E/0511 |  | SO on sewer network | NZ3376042870 | GB103024077540 | Pittington Beck from Coalford to Old Durham Beck | COALFORD BECK, TRIBUTARY OF |  |  | Commissioned pre-2016 - full year data expected | 2.75 | 7 | 99.99%
Northumbrian Water | SHERBURN SSO MANHOLE NO. 34 | 6NW801383 | 245/E/0513 | 245/E/0513 |  | SO on sewer network | NZ3192041820 | GB103024077490 | Old Durham Beck from Source to Pittington Beck | SHERBURNHOUSE BECK |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | SHERBURN SSO MANHOLE NO. 33 Mill Lane | 6NW801674 | 245/1297 | 245/1297 |  | SO on sewer network | NZ3192041820 | GB103024077490 | Old Durham Beck from Source to Pittington Beck | SHERBURNHOUSE BECK |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | SHERBURN SEWAGE TREATMENT WORKS | 6NW800777 | 245/1248 | 245/1248 | 245/1248-03 | Storm tank at WwTW | NZ3165041830 | GB103024077490 | Old Durham Beck from Source to Pittington Beck | SHERBURN BECK |  |  | Commissioned in 2020 - full year data expected | 903.3942 | 70 | 100%
Northumbrian Water | SHIBDON ROAD CSO | 6NW801091 | 234/1021 | 234/1021 |  | SO on sewer network | NZ1983562379 | GB510302310200 | TYNE | DERWENT ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 2.1 | 4 | 99.9%
Northumbrian Water | SHIELDS ROAD CSO | 6NW801282 | 245/1114 | 245/1114 |  | SO on sewer network | NZ2802452071 | GB103024077624 | Wear DS of Lumley Park Burn to Tidal Limit | RIVER WEAR |  |  | Commissioned pre-2016 - full year data expected | 218.25 | 51 | 99.97%
Northumbrian Water | SHILBOTTLE CSO NO. 2 A015 | 6NW800861 | 223/G/0087 | 223/G/0087 |  | SO on sewer network | NU2122108615 | GB103022076720 | Tyelaw Burn Catchment (trib of Coquet) | TYELAW BURN |  |  | Commissioned pre-2016 - full year data expected | 106 | 36 | 99.82%
Northumbrian Water | SHILBOTTLE SEWAGE TREATMENT WORKS | 6NW800696 | 223/0991 | 223/0991 | 223/0991-02 | Storm tank at WwTW | NU2167008510 | GB103022076720 | Tyelaw Burn Catchment (trib of Coquet) | TYELAW BURN |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | CSO AT SHILDON | 6NW801155 | 25/03/1216 | 25/03/1216 |  | SO on sewer network | NZ2452025230 | GB103025072400 | Woodham Burn from Source to Rushyford beck | TRIB OF WOODHAM BURN |  |  | Commissioned pre-2016 - full year data expected | 10 | 10 | 99.99%
Northumbrian Water | SHILDON CSO WEST ROAD AUCKLAND | 6NW801143 | EPRAB3691WJ | EPRAB3691WJ |  | SO on sewer network | NZ2268726227 | GB103025072400 | Woodham Burn from Source to Rushyford beck | TRIB OF THE WOODHAM BURN |  |  | Commissioned pre-2016 - full year data expected | 1.25 | 5 | 99.86%
Northumbrian Water | SHINCLIFFE (A177) CSO | 6NW801308 | 245/1285 | 245/1285 |  | SO on sewer network | NZ2876741031 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | RIVER WEAR |  |  | Commissioned pre-2016 - full year data expected | 7.75 | 11 | 99.67%
Northumbrian Water | SHINCLIFFE SSO MANHOLE NO. 2 | 6NW801306 | 245/E/0499 | 245/E/0499 | A1 | Storm discharge at pumping station | NZ2872041000 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | WEAR |  |  | Commissioned pre-2016 - full year data expected | 14.75 | 8 | 99.99%
Northumbrian Water | SHINCLIFFE NO 2 PS | 6NW800562 | 245/A/0463 | 245/A/0463 | 245/A/0463-02 | Storm discharge at pumping station | NZ2930041340 | GB103024077470 | Old Durham Beck from Chapman Beck to Wear | OLD DURHAM BECK |  |  | Commissioned in 2020 - full year data expected | 24.3308 | 12 | 100%
Northumbrian Water | SHINEY ROW FOOTBRIDGE CSO | 6NW801413 | 245/1368 | 245/1368 |  | SO on sewer network | NZ3288752353 | GB103024077630 | Herrington Burn from Source to Lumley Park Burn | HERRINGTON BURN |  |  | Commissioned pre-2016 - full year data expected | 47 | 23 | 99.92%
Northumbrian Water | SHOREGATE CSO | 6NW800831 | 210/1347 | 210/1347 |  | SO on sewer network | NT9979752582 | GB510202110000 | TWEED | RIVER TWEED (SALINE ESTUARY) |  | Spittal | Commissioned pre-2016 - full year data expected | 6.8667 | 4 | 95.77%
Northumbrian Water | SHOTLEY BRIDGE CSO DER0004 | 6NW800948 | 234/1107 | 234/1107 |  | SO on sewer network | NZ0900152376 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | TRIBUTARY OF RIVER DERWENT |  |  | Commissioned pre-2016 - full year data expected | 0.5 | 1 | 74.58% | Sensor failure / issue | Resolved - June
Northumbrian Water | SHOTLEY BRIDGE HOSPITAL CSO | 6NW800956 | 234/1116 | 234/1116 |  | SO on sewer network | NZ1010052600 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | TINKERHILL GILL |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 81.02% | Sensor failure / issue | Resolved - July
Northumbrian Water | SHOTTON LANE CSO | 6NW801506 | 255/1194 | 255/1194 |  | SO on sewer network | NZ4025049490 | 367 | #N/A | CALFPASTURE BURN |  |  | Commissioned pre-2016 - full year data expected | 370.25 | 57 | 99.67%
Northumbrian Water | SILVER LONNEN CSO (NC030) | 6NW800271 | 235/1938 | 235/1938 |  | SO on sewer network | NZ1965463974 | GB510302310200 | TYNE | RIVER TYNE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 304 | 69 | 99.6% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | SIMONSIDE CSO | 6NW801439 | 226/1124 | 226/1124 |  | SO on sewer network | NZ3373775609 | GB103022076190 | Seaton Burn from Source to Tidal Limit | SEATON BURN |  | Seaton Sluice | Commissioned pre-2016 - full year data expected | 1.9 | 10 | 99.95%
Northumbrian Water | SIXTH ST SSO | 6NW800964 | 244/0873 | 244/0873 |  | SO on sewer network | NZ1192050530 | GB103024077330 | Smallhope Burn from Source to Browney, Stocke | STOCKERLEY BURN, TRIBUTARY OF |  |  | Commissioned pre-2016 - full year data expected | 7.75 | 14 | 95%
Northumbrian Water | SKINNINGROVE SEWAGE PUMPING STATION 1 | 6NW800676 | 25/06/1033 | 25/06/1033 | 25/06/1033-01 | Storm discharge at pumping station | NZ7132020110 | GB103025071950 | Kilton Beck from Middle Gill Beck to North Sea | NORTH SEA |  |  | Commissioned in 2020 - full year data expected | 458 | 59 | 100%
Northumbrian Water | SKINNINGROVE SEWAGE PUMPING STATION 2 | 6NW800677 | 25/06/1033 | 25/06/1033 | 25/06/1033-02 | Storm discharge at pumping station | NZ7132020110 | GB103025071950 | Kilton Beck from Middle Gill Beck to North Sea | NORTH SEA |  |  | Commissioned in 2020 - full year data expected | 5.225 | 1 | 100%
Northumbrian Water | SKIPPERS LANE INDUSTRIAL ESTATE PS | 6NW801592 | 254/1849 | 254/1849 |  | SO on sewer network | NZ5262020100 | 10 | #N/A | SPENCER BECK |  |  | Commissioned pre-2016 - full year data expected | 15.75 | 6 | 99.99%
Northumbrian Water | SLAGGYFORD SPS | 6NW800486 | 232/0992 | 232/0992 | A1 | Storm discharge at pumping station | NY6795052330 | GB103023075531 | South Tyne from Black Burn to Tipalt Burn | SOUTH TYNE TRIB |  |  | Commissioned in 2020 - full year data expected | 21.3417 | 6 | 99.81%
Northumbrian Water | SLALEY STW CSO INLET | 6NW800141 | 233/1178 | 233/1178 | 233/1178-03 | Inlet SO at WwTW | NY9840057300 | GB103023075650 | March Burn Catchment (trib of Tyne) | FLOTHERS BURN |  |  | Commissioned in 2020 - full year data expected | 8.6319 | 21 | 100%
Northumbrian Water | SLALEY STW Primary treated storm | 6NW800810 | 233/1178 | 233/1178 | 233/1178-04 | Inlet SO at WwTW | NY9840057300 | GB103023075650 | March Burn Catchment (trib of Tyne) | FLOTHERS BURN |  |  | Commissioned in 2020 - full year data expected | 17.94 | 62 | 100%
Northumbrian Water | SMAILES LANE CSO G15 | 6NW801007 | 234/1158 | 234/1158 |  | SO on sewer network | NZ1536758832 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | LOW SPEN BURN |  |  | Commissioned pre-2016 - full year data expected | 154.75 | 40 | 99.2%
Northumbrian Water | SMITH STREET PUMPING STATION | 6NW800597 | 235/1652 | 235/1652 | 235/1652-01 | Storm discharge at pumping station | NZ3534566008 | GB510302310200 | TYNE | TYNE SALINE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 133.5 | 16 | 99.99%
Northumbrian Water | A CSO AT SMITHS DOCK ROAD | 6NW800669 | QC.25/04/1590 | QC.25/04/1590 | S1 | Storm discharge at pumping station | NZ5290022000 | GB510302509900 | TEES | THE RIVER TEES |  |  | Commissioned in 2020 - full year data expected | 0 | 0 | 100%
Northumbrian Water | CSO & PUMPING STN DOCK ROAD | 6NW800664 | 25/04/1599 | 25/04/1599 |  | Storm discharge at pumping station | NZ5279021910 | GB510302509900 | TEES | TIDAL RIVER TEES |  |  | Commissioned in 2017 - full year data expected | 0 | 0 | 92.95%
Northumbrian Water | SMITHY LANE CSO | 6NW800325 | 235/1558 | 235/1558 |  | SO on sewer network | NZ2597058230 | GB103023075670 | Team from Source to Tyne | TRIBUTARY OF RIVER TEAM |  |  | Commissioned in 2016 - full year data expected | 0 | 0 | 99.97%
Northumbrian Water | SNOWDON ROAD PS | 6NW800647 | 254/1511 | QR.25/04/1511 | A | Storm discharge at pumping station | NZ4917120890 | 10 | #N/A | River Tees |  |  | Commissioned in 2020 - full year data expected | 0 | 0 | 100%
Northumbrian Water | SNOWS GREEN ROAD CSO (DER010) | 6NW800957 | 234/1165 | 234/1165 |  | SO on sewer network | NZ1005053260 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | DERWENT |  |  | Commissioned pre-2016 - full year data expected | 2.75 | 5 | 86.28% | Comms failure / issue | Resolved - March
Northumbrian Water | BRUS SEWAGE PUMPING STATION Soft Leas | 6NW800666 | 255/5021 | QC.25/05/5020 | A1 | Storm discharge at pumping station | NZ5281934509 | GB650301500005 | Tees Coastal | North Sea |  |  | Commissioned in 2019 - full year data expected | 178.6694 | 28 | 100%
Northumbrian Water | SOLINGEN ESTATE CSO | 6NW801648 | EPRAB3090EN | EPRAB3090EN |  | SO on sewer network | NZ3207980783 | GB510302203200 | BLYTH (N) | RIVER BLYTH (SALINE ESTUARY) |  | Blyth South Beach | Commissioned pre-2016 - full year data expected | 1.0333 | 3 | 98.77%
Northumbrian Water | SOUTH BENWELL ROAD CSO | 6NW800283 | 235/1958 | 235/1958 |  | SO on sewer network | NZ2138063404 | GB510302310200 | TYNE | RIVER TYNE |  |  | Commissioned in 2018 - full year data expected | 236.5408 | 47 | 100%
Northumbrian Water | SOUTH BLYTH HARBOUR CSO | 6NW800365 | 226/1210 | 226/1210 |  | SO on sewer network | NZ3208080790 | GB510302203200 | BLYTH (N) | RIVER BLYTH (SALINE ESTUARY) |  | Blyth South Beach | Commissioned pre-2016 - full year data expected | 371.9667 | 45 | 100%
Northumbrian Water | SOUTH CHURCH CSO | 6NW801132 | EPRBB3494EG | EPRBB3494EG |  | SO on sewer network | NZ2191628507 | GB103024072730 | Gaunless from Hummer Beck to Wear | RIVER GAUNLESS |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 98.4%
Northumbrian Water | SOUTH CLEATLAM CSO | 6NW801677 | #TBC | Permit Anomaly | To be permitted for storm | SO on sewer network | NZ1255718039 | GB103025072200 | Langley Bk and Westholme Bk frm Sudburn Bk to Tees | Newham Beck |  |  | Commissioned pre-2016 - full year data expected | 0.5 | 2 | 97.74%
Northumbrian Water | SOUTH EAST VIEW CSO | 6NW800422 | 255/1214 | 255/1214 |  | SO on sewer network | NZ4456341187 | 367 | #N/A | BLACKHILLS GILL |  |  | Commissioned pre-2016 - full year data expected | 5.25 | 13 | 99.97%
Northumbrian Water | MILLBURNGATE CSO SOUTH END | 6NW800665 | 245/1286 | Permit Anomaly - EO permit 245/1286 | To be permitted for storm | Storm discharge at pumping station | NZ5255429206 | 10 | #N/A | Culverted watercourse to North Sea |  |  | Commissioned pre-2016 - full year data expected | 0.13333 | 2 | 93.01%
Northumbrian Water | SOUTH FARM CSO | 6NW800997 | 244/0941 | 244/0941 |  | SO on sewer network | NZ1479043230 | GB103024077290 | Hedleyhope Burn from Source to Deerness | RAVENSBUSH BURN |  |  | Commissioned pre-2016 - full year data expected | 1 | 3 | 94.32%
Northumbrian Water | SOUTH GREEN LANE CSO | 6NW800336 | 225/0962 | 225/0962 | A1 | Storm discharge at pumping station | NZ2730486575 | GB103022077062 | Wansbeck from Bothal Burn to North Sea | BLACKCLOSE DENE |  |  | Commissioned in 2019 - full year data expected | 0.545 | 4 | 100%
Northumbrian Water | SOUTH MOOR MEMORIAL PARK SSO | 6NW801062 | 245/1179 | 245/1179 |  | SO on sewer network | NZ1888051190 | GB103024077590 | Twizell Burn from Source to Cong Burn | STANLEY BURN |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 92.53%
Northumbrian Water | SOUTH MOOR ROAD FOOTBALL CLUB CSO | 6NW800262 | 245/1262 | 245/1262 |  | SO on sewer network | NZ1909451305 | GB103024077590 | Twizell Burn from Source to Cong Burn | STANLEY BURN |  |  | Commissioned in 2016 - full year data expected | 0 | 0 | 98.52%
Northumbrian Water | SOUTH OF COCKFIELD STW CSO TE63 | 6NW800990 | 242/1058 | 242/1058 |  | SO on sewer network | NZ1350024630 | GB103024072690 | Gaunless from Source to Hummer Beck | GAUNLESS TRIB |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 54.37% | Comms failure / issue | Resolved - August
Northumbrian Water | SOUTH OF ROOKWOOD CSO NTY 003 | 6NW800311 | 226/1268 | 226/1268 |  | SO on sewer network | NZ2447843434 | GB103024077551 | Browney from Smallhope Burn Deerness confl | SEATON BURN |  |  | Commissioned in 2017 - full year data expected | 7.25 | 5 | 66.97% | Comms failure / issue | Resolved - November
Northumbrian Water | SOUTH PARK CSO DL035 | 6NW800344 | 25/03/1230 | 25/03/1230 |  | SO on sewer network | NZ2839612932 | GB103025072596 | Skerne from Demons Beck to Tees | RIVER SKERNE |  |  | Commissioned in 2017 - full year data expected | 233 | 39 | 99.99%
Northumbrian Water | SOUTH PARK EAST CSO | 6NW801326 | 253/1280 | 253/1280 |  | SO on sewer network | NZ2884813759 | GB103025072596 | Skerne from Demons Beck to Tees | SKERNE |  |  | Commissioned pre-2016 - full year data expected | 1.25 | 5 | 99.71%
Northumbrian Water | SOUTH ROAD NO 18 CSO | 6NW800820 | NPSWQD006905 | NPSWQD006905 |  | SO on sewer network | NT9942128106 | GB102021072930 | Wooler Water from Harthope Burn to Till | WOOLER WATER |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | WOOLER CSO | 6NW800821 | 210/D/0271 | 210/D/0271 |  | SO on sewer network | NT9944028110 | GB102021072930 | Wooler Water from Harthope Burn to Till | WOOLER WATER |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | SOUTH SHIELDS INTERCEPTOR BS/104 | 6NW800368 | 235/B/0170 | 235/B/0170 |  | SO on sewer network | NZ3343764674 | GB103023075690 | Don from Source to Tidal Limit | RIVER DON |  |  | Commissioned in 2018 - full year data expected | 786.3014 | 88 | 100%
Northumbrian Water | SOUTH SHORE ROAD EAST PUMPING STN | 6NW800545 | 235/1658 | 235/1658 | 235/1658-01 | Storm discharge at pumping station | NZ2695063370 | GB510302310200 | TYNE | TYNE SALINE ESTUARY |  |  | Commissioned in 2020 - full year data expected | 525.7592 | 103 | 100%
Northumbrian Water | SOUTH SHORE ROAD CSO | 6NW801242 | 235/1661 | 235/1661 |  | SO on sewer network | NZ2653363864 | GB510302310200 | TYNE | TYNE SALINE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 56.2994 | 35 | 91.55%
Northumbrian Water | 5 SOUTH STREET CSO, CROOKHALL | 6NW800963 | 244/0919 | 244/0919 |  | SO on sewer network | NZ1214050620 | GB103024077330 | Smallhope Burn from Source to Browney, Stocke | STOCKERLEY BURN TRIBUTARY |  |  | Commissioned pre-2016 - full year data expected | 0.75 | 2 | 91.64%
Northumbrian Water | SOUTH STREET CSO ST003 | 6NW800395 | 254/1825 | 254/1825 |  | SO on sewer network | NZ3738723336 | GB103025072360 | Billingham Beck from Bishopton Bck to Brierle | CULVERTED W/C TO BISHOPTON BEC |  |  | Commissioned pre-2016 - full year data expected | 1 | 4 | 95.03%
Northumbrian Water | SOUTH TERRACE CSO (G003) | 6NW800982 | 234/1147 | 234/1147 |  | SO on sewer network | NZ1209057630 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | TONGUE BURN |  |  | Commissioned pre-2016 - full year data expected | 4.5 | 4 | 99.99%
Northumbrian Water | SOUTH VIEW CSO | 6NW800904 | 25/01/0915 | 25/01/0915 |  | SO on sewer network | NY9740023950 | GB103025072511 | Tees from Maize Beck to Percy Beck | HEUGH SIKE |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.13%
Northumbrian Water | SOUTH WYLAM PUMPING STATION | 6NW800985 | 233/1039 | 233/1039 | 233/1039-01 | Storm discharge at pumping station | NZ1209064610 | 8 | #N/A | STANLEY BURN |  |  | Commissioned pre-2016 - full year data expected | 221.5 | 69 | 97.95% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | SOUTHFIELD CSO | 6NW800863 | NPSWQD002462 | NPSWQD002462 |  | SO on sewer network | NU2229131513 | GB620301100000 | Farne Islands to Newton Haven | N. SEA & UN-NAMED WATERCOURSE |  | Seahouses North | Commissioned pre-2016 - full year data expected | 0.033333 | 1 | 100%
Northumbrian Water | SOUTHFIELD ROAD CSO | 6NW801140 | 235/1507 | 235/1507 |  | SO on sewer network | NZ2168660319 | GB103023075670 | Team from Source to Tyne | BLACK BURN TRIB |  |  | Commissioned pre-2016 - full year data expected | #N/A | #N/A | 0% | Comms failure / issue | Scheduled
Northumbrian Water | SOUTHFIELDS CSO | 6NW801205 | 245/1280 | 245/1280 |  | SO on sewer network | NZ2548652509 | GB103024077600 | Cong Burn from Twizell Burn to Wear | CHESTER BURN, TRIBUTARY OF |  |  | Commissioned pre-2016 - full year data expected | 15 | 7 | 52.19% | Comms failure / issue | Resolved - November
Northumbrian Water | SOWERBY CRESCENT/NORTH RD JUNCT CSO | 6NW801588 | 25/04/1570 | 25/04/1570 |  | SO on sewer network | NZ5217108122 | GB103025071890 | Leven from Source to Tame | RIVER LEVEN |  |  | Commissioned pre-2016 - full year data expected | 6.5 | 9 | 99.88%
Northumbrian Water | SPILLERS PUMPING STATION | 6NW800537 | 235/1760 | 235/1760 | 235/1760-01 | Storm discharge at pumping station | NZ2678063750 | GB510302310200 | TYNE | RIVER TYNE SALINE ESTUARY |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | SPITTAL QUAY CSO (BT7) | 6NW800842 | 210/1360 | 210/1360 |  | SO on sewer network | NU0018151930 | GB510202110000 | TWEED | RIVER TWEED (SALINE ESTUARY) |  | Spittal | Commissioned pre-2016 - full year data expected | 214.4 | 57 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | SPRING COURT CSO DL006 | 6NW801263 | 253/1275 | 253/1275 |  | SO on sewer network | NZ2748216123 | GB103025072596 | Skerne from Demons Beck to Tees | WEST BECK |  |  | Commissioned pre-2016 - full year data expected | 7.5 | 7 | 99.99%
Northumbrian Water | SPRINGFIELD COTTAGES CSO | 6NW800915 | 233/1243 | 233/1243 |  | SO on sewer network | NY9892064220 | GB103023075801 | Tyne from Watersmeet to Tidal Limit | RIVER TYNE |  |  | Commissioned pre-2016 - full year data expected | 0.25 | 1 | 99.95%
Northumbrian Water | SPRING WAY CSO ST021 | 6NW801528 | 254/1827 | 254/1827 |  | SO on sewer network | NZ4303017882 | GB103025072550 | Lustrum Beck Catchment (trib of Tees) | HARTBURN BECK |  |  | Commissioned pre-2016 - full year data expected | 21.25 | 27 | 92.25%
Northumbrian Water | SPRINGWELL PARK CSO | 6NW801415 | 235/1704 | 235/1704 |  | SO on sewer network | NZ3295164058 | GB103023075690 | Don from Source to Tidal Limit | MONKTON BURN |  |  | Commissioned pre-2016 - full year data expected | 304.75 | 35 | 99.72%
Northumbrian Water | WESTERN ROAD/ROSEHILL ROAD P ST | 6NW800586 | 235/1521 | 235/1521 | 235/1521-01 | Storm discharge at pumping station | NZ3205066100 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | June 2021 | 74.75 | 23 | 99.47%
Northumbrian Water | ST AIDENS PARK CSO | 6NW800222 | 232/1011 | 232/1011 |  | SO on sewer network | NY8882767652 | GB103023075710 | South Tyne from Allen to North Tyne | RIVER SOUTH TYNE |  |  | Commissioned in 2017 - full year data expected | 0.25 | 1 | 99.99%
Northumbrian Water | ST ANDREWS ROAD CSO | 6NW800265 | 235/1715 | 235/1715 |  | SO on sewer network | NZ1967654170 | GB103023075670 | Team from Source to Tyne | UNNAMED TRIB HOUGHWELL BURN |  |  | Commissioned pre-2016 - full year data expected | 92 | 35 | 99.61% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | HOWLE BECK OVERFLOWS (MARSKE CEMETE ST GERMAINS LANE | 6NW801618 | 25/06/1017 | 25/06/1017 |  | SO on sewer network | NZ6417022730 | GB650301500005 | Tees Coastal | NORTH SEA |  | Marske | Commissioned pre-2016 - full year data expected | 31 | 16 | 100%
Northumbrian Water | ST HELENS LANE CSO | 6NW800916 | 233/1090 | 233/1090 |  | SO on sewer network | NY9867764397 | GB103023075801 | Tyne from Watersmeet to Tidal Limit | RIVER TYNE |  |  | Commissioned pre-2016 - full year data expected | 29.5 | 26 | 99.99%
Northumbrian Water | PRINCES/WOODBINE(ST HELENS ST.)CSO | 6NW800914 | 233/1245 | 233/1245 |  | SO on sewer network | NY9900064400 | GB103023075801 | Tyne from Watersmeet to Tidal Limit | TYNE |  |  | Commissioned pre-2016 - full year data expected | 0.5 | 2 | 99.71%
Northumbrian Water | ST IVES ROAD CSO | 6NW800977 | 234/1140 | 234/1140 |  | SO on sewer network | NZ1261052430 | GB103023074780 | Pont Burn Catchment (trib of Derwent) | TRIB PONT BURN |  |  | Commissioned pre-2016 - full year data expected | 1.75 | 4 | 99.59%
Northumbrian Water | POINT M ST JAMES CHURCH CSO | 6NW801642 | 225/1073 | 225/1073 |  | SO on sewer network | NZ1952086120 | GB103022077061 | Wansbeck from Font to Bothal Burn | COTTING BURN |  |  | Commissioned pre-2016 - full year data expected | 16 | 7 | 99.95%
Northumbrian Water | WARKWORTH SEWERAGE SYSTEM SSO MH NO St Lawrence Court | 6NW800867 | 223/B/0057 | 223/B/0057 |  | SO on sewer network | NU2460006000 | GB510302203000 | COQUET | COQUET, TIDAL WATERS |  | Warkworth & Amble Links | Commissioned pre-2016 - full year data expected | 19.1333 | 3 | 100%
Northumbrian Water | ST LEONARDS ROAD SSO | 6NW801606 | 25/06/0998 | 25/06/0998 |  | SO on sewer network | NZ6001015290 | GB103025071970 | Skelton Beck Catch (Saltburn) trib of North Sea | HUTTON BECK |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.87%
Northumbrian Water | ST LUKES ROAD | 6NW800380 | 245/1372 | 245/1372 |  | SO on sewer network | NZ3543057320 | GB510302402900 | WEAR | WEAR (SALINE ESTUARY) |  |  | Commissioned in 2020 - full year data expected | 1.2686 | 2 | 100%
Northumbrian Water | ST MARYS PRIMARY SCHOOL CSO | 6NW801631 | 234/1173 | 234/1173 |  | SO on sewer network | NZ0894652307 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | BACKSTONE BURN (DERWENT) |  |  | Commissioned pre-2016 - full year data expected | 73.75 | 28 | 90.2% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | ST MARYS SEWAGE PUMPING STATION | 6NW800551 | EPRBB3597VK | EPRBB3597VK | A1 | Storm discharge at pumping station | NZ1844580297 | GB103022076220 | Duddo Burn from Source to Blyth | DUDDO BURN |  |  | Commissioned in 2020 - full year data expected | 392.1464 | 29 | 96.96%
Northumbrian Water | ST NICHOLAS HOSPITAL SSO | 6NW801169 | 235/1548 | 235/1548 |  | SO on sewer network | NZ2422069510 | GB103023075780 | Ouse Burn from Source to Tyne | OUSE BURN |  |  | Commissioned pre-2016 - full year data expected | 3.25 | 2 | 91.44%
Northumbrian Water | ST AIDANS SEWAGE PUMPING STATION | 6NW800465 | 221/1073 | 221/1073 | 221/1073-01 | Storm discharge at pumping station | NU2151032590 | GB650301440000 | Northumberland North | NORTH SEA |  | Seahouses North | Commissioned in 2016 - full year data expected | 35.7333 | 3 | 91.25%
Northumbrian Water | ESH WINNING CSO POINT A2 STAGS HEAD | 6NW801080 | 244/1015 | 244/1015 |  | SO on sewer network | NZ1921141549 | GB103024077270 | Deerness from Source to Hedleyhope Burn | River Deerness |  |  | Commissioned pre-2016 - full year data expected | 130.25 | 32 | 99.49%
Northumbrian Water | STAIGS GARTH SPS | 6NW800854 | 222/0853 | 222/0853 | 222/0853-01 | Storm discharge at pumping station | NU1856113855 | GB103022076350 | Aln from Edlingham Burn to Tidal Limit | R ALN |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 98.24%
Northumbrian Water | STAINDROP PUMPING STATION | 6NW800240 | 252/1020 | 252/1020 | A | Storm discharge at pumping station | NZ1425019750 | GB103025072270 | Sudburn Beck from Source to Langley Beck | SUDBURN BECK |  |  | Commissioned pre-2016 - full year data expected | 994.5 | 70 | 99.17% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | STAINDROP SEWAGE TREATMENT WORKS | 6NW800730 | 25/02/1109 | 25/02/1109 | A2 | Storm tank at WwTW | NZ1430019730 | GB103025072200 | Langley Bk and Westholme Bk frm Sudburn Bk to Tees | LANGLEY BECK |  |  | Commissioned in 2020 - full year data expected | 0.3975 | 3 | 100%
Northumbrian Water | STAINSBY ROAD CSO | 6NW801568 | 254/1816 | 254/1816 |  | SO on sewer network | NZ4723017880 | GB510302509900 | TEES | OLD RIVER TEES |  |  | Commissioned pre-2016 - full year data expected | 26.75 | 8 | 46.16% | Comms failure / issue | Scheduled
Northumbrian Water | STAINTON CSO | 6NW800934 | 252/1052 | 252/1052 |  | SO on sewer network | NZ0711818504 | GB103025072200 | Langley Bk and Westholme Bk frm Sudburn Bk to Tees | BLACK BECK TRIBUTARY |  |  | Commissioned pre-2016 - full year data expected | 19.75 | 5 | 97.77%
Northumbrian Water | STAMFORDHAM CSO | 6NW800230 | 226/G/0092 | 226/G/0092 |  | SO on sewer network | NZ0817771830 | GB103022076840 | Pont from Fenwick Burn to Med Burn | PONT |  |  | Commissioned in 2017 - full year data expected | 64.5 | 31 | 94.44%
Northumbrian Water | STAMFORDHAM ROAD PUMPING STATION | 6NW800682 | 235/1394 | 235/1394 | 235/1394-01 | Storm discharge at pumping station | NZ1866768300 | GB103023075780 | Ouse Burn from Source to Tyne | OUSE BURN |  |  | Commissioned in 2020 - full year data expected | 101.0853 | 13 | 99.93%
Northumbrian Water | STAMFORDHAM SEWAGE TREATMENT WORKS | 6NW800716 | 226/A/0875 | 226/A/0875 |  | Storm tank at WwTW | NZ0843571877 | GB103022076840 | Pont from Fenwick Burn to Med Burn | River Pont |  |  | Commissioned in 2020 - full year data expected | 153.9497 | 19 | 100%
Northumbrian Water | STRANGHOW ROAD NO2 CSO | 6NW801621 | 25/06/1025 | 25/06/1025 |  | SO on sewer network | NZ6716117742 | GB103025071960 | Saltburn Gill Catch trib of North Sea | HOLME BECK (SKELTON CATCHMENT |  |  | Commissioned pre-2016 - full year data expected | 286.75 | 62 | 99.98% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | STANHOPE CLOSE CSO SU 26 | 6NW801426 | 245/1356 | 245/1356 |  | SO on sewer network | NZ3327049250 | GB103024077580 | Lumley Park Burn from Source to Herrington Burn | RAINTON BURN |  |  | Commissioned pre-2016 - full year data expected | 148.5 | 46 | 99.88%
Northumbrian Water | STANHOPE STW | 6NW800712 | 241/1100 | 241/1100 | 241/1100-03 | Storm tank at WwTW | NZ0085037980 | GB103024077461 | Wear from Middlehope Burn to Houselop Beck | WEAR |  |  | Commissioned in 2020 - full year data expected | 453.4103 | 53 | 100%
Northumbrian Water | STANHOPE SWIMMING POOL CSO | 6NW800912 | EPRBP3729GJ | EPRBP3729GJ |  | SO on sewer network | NY9927439202 | GB103024077461 | Wear from Middlehope Burn to Houselop Beck | RIVER WEAR |  |  | Commissioned pre-2016 - full year data expected | 20 | 12 | 31.55% | Comms failure / issue | Resolved - December
Northumbrian Water | STANNINGTON VILLAGE PUMPING STATION | 6NW800524 | 226/1000 | 226/1000 | A1 | Storm discharge at pumping station | NZ2132678968 | GB103022077052 | Blyth from Pont to Tidal Limit | CATRAW BURN (BLYTH) |  |  | Commissioned in 2020 - full year data expected | 1311.5992 | 71 | 100%
Northumbrian Water | STAPLETON SPS | 6NW800534 | 252/D/0167 | 252/D/0167 | A1 | Storm discharge at pumping station | NZ2654712120 | GB103025072190 | Tees from River Greta to River Skerne | RIVER TEES |  |  | Commissioned in 2019 - full year data expected | 0.14333 | 1 | 99.58%
Northumbrian Water | STARTFORTH PS | 6NW800499 | 252/0992 | 252/0992 | A | Storm discharge at pumping station | NZ0445016630 | GB103025072170 | Deepdale Beck from Source to River Tees | DEEPDALE BECK (TEES) |  |  | Commissioned in 2020 - full year data expected | 41.8708 | 11 | 100%
Northumbrian Water | STATION BANK CSO | 6NW801011 | 233/1024 | 233/1024 |  | SO on sewer network | NZ1535165135 | GB510302310200 | TYNE | RIVER TYNE ESTUARINE WATERS |  |  | Commissioned pre-2016 - full year data expected | 149.25 | 54 | 99.85%
Northumbrian Water | STATION BANK (DU21) | 6NW801384 | 245/1296 | 245/1296 |  | SO on sewer network | NZ3107042270 | GB103024077540 | Pittington Beck from Coalford to Old Durham Beck | PITTINGTON BECK |  |  | Commissioned pre-2016 - full year data expected | 16.25 | 23 | 99.97%
Northumbrian Water | STATION HOTEL SPS | 6NW800675 | 256/1078 | 256/1078 | A1 | Storm discharge at pumping station | NZ7186418097 | GB103025071940 | Middle Gill Beck from Source to Kilton Beck | LOFTUS BECK |  |  | Commissioned pre-2016 - full year data expected | 229.5 | 37 | 99.98%
Northumbrian Water | BARDON MILL (STATION HOUSE) P.S. | 6NW800490 | 232/0989 | 232/0989 | 232/0989-01 | Storm discharge at pumping station | NY7791064540 | GB103023075540 | Brackies Burn to catchment (trib of South Tyne) | CHAINLEY BURN |  |  | Commissioned in 2020 - full year data expected | 106.2483 | 33 | 99.99%
Northumbrian Water | STATION LANE CSO | 6NW800304 | 245/1313 | 245/1313 |  | SO on sewer network | NZ2536052630 | GB103024077600 | Cong Burn from Twizell Burn to Wear | CHESTER BURN, TRIBUTARY OF |  |  | Commissioned in 2019 - full year data expected | 2.25 | 5 | 99.98%
Northumbrian Water | STATION ROAD CSO | 6NW800907 | 233/1253 | 233/1253 |  | SO on sewer network | NY9887064090 | GB103023075801 | Tyne from Watersmeet to Tidal Limit | TYNE |  |  | Commissioned pre-2016 - full year data expected | 172.25 | 20 | 99.95%
Northumbrian Water | STATION ROAD CSO G020 | 6NW801456 | 235/1702 | 235/1702 |  | SO on sewer network | NZ3426262739 | GB103023075801 | Tyne from Watersmeet to Tidal Limit | RIVER DON |  |  | Commissioned pre-2016 - full year data expected | 578.75 | 56 | 99.79% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | STATION ROAD CSO | 6NW801389 | 245/1284 | 245/1284 |  | SO on sewer network | NZ3108353868 | GB103023075801 | Tyne from Watersmeet to Tidal Limit | RIVER WEAR |  |  | Commissioned pre-2016 - full year data expected | 172.2333 | 61 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | STATION ROAD STORM SEWAGE OVERFLOW | 6NW801561 | 254/1809 | 254/1809 |  | SO on sewer network | NZ4522022940 | GB103023075801 | Tyne from Watersmeet to Tidal Limit | BILLINGHAN BECK |  |  | Commissioned pre-2016 - full year data expected | 124.75 | 46 | 98.98%
Northumbrian Water | STATION ROAD CSO | 6NW801548 | 255/1221 | 255/1221 |  | SO on sewer network | NZ4391043370 | GB103023075801 | Tyne from Watersmeet to Tidal Limit | HORDEN BURN |  |  | Commissioned pre-2016 - full year data expected | 39.75 | 28 | 97.89%
Northumbrian Water | STATION ROAD CSO | 6NW801609 | 256/1067 | 256/1067 |  | SO on sewer network | NZ6019425998 | GB103023075801 | Tyne from Watersmeet to Tidal Limit | NORTH SEA |  | Redcar Coatham | Commissioned pre-2016 - full year data expected | 20.5333 | 15 | 99.74%
Northumbrian Water | STATION ROAD CSO G020 | 6NW801029 | 234/1127 | 234/1127 |  | SO on sewer network | NZ1693758726 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | DERWENT |  |  | Commissioned pre-2016 - full year data expected | 87.75 | 33 | 99.86%
Northumbrian Water | STATION VILLAS CSO | 6NW800264 | 235/1709 | 235/1709 |  | SO on sewer network | NZ1968054170 | GB103023075670 | Team from Source to Tyne | HOUGHWELL BURN |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.98%
Northumbrian Water | STELLA ROAD CSO | 6NW800251 | 233/1225 | 233/1225 |  | SO on sewer network | NZ1744263972 | 8 | #N/A | CLVRT WATERCRSE RIVER TYNE |  |  | Commissioned in 2016 - full year data expected | 6.25 | 3 | 99.98%
Northumbrian Water | STEPHENSON STREET PUMPING STATION | 6NW800588 | 235/1689 | 235/1689 | 235/1689-01 | Storm discharge at pumping station | NZ3271066100 | GB510302310200 | TYNE | TYNE |  |  | Commissioned in 2019 - full year data expected | 137.5 | 49 | 99.99%
Northumbrian Water | AYCLIFFE (STEPHENSON WAY) PS | 6NW800542 | 25/03/1243 | 25/03/1243 |  | Storm discharge at pumping station | NZ2910023660 | GB103025072391 | Skerne form Woodham Burn to Demons Beck | RIVER SKERNE |  |  | Commissioned in 2020 - full year data expected | 71.7419 | 19 | 100%
Northumbrian Water | STEPPEY LANE CSO A020 | 6NW800864 | 222/0860 | 222/0860 |  | SO on sewer network | NU2373410923 | 6 | #N/A | HIPS BURN |  |  | Commissioned pre-2016 - full year data expected | 1.1667 | 4 | 99.99%
Northumbrian Water | STEPPING STONES CSO | 6NW800846 | 223/0949 | 223/0949 |  | SO on sewer network | NU0631001741 | GB103022076692 | Coquet from Holystone Burn to Forest Burn | RIVER COQUET |  |  | Commissioned pre-2016 - full year data expected | 224.25 | 27 | 60.66% | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
Northumbrian Water | LESBURY (STEPPY LANE) PUMPING STATI | 6NW800471 | 222/0868 | 222/0868 | 222/0868-01 | Storm discharge at pumping station | NU2384011580 | GB103022076350 | Aln from Edlingham Burn to Tidal Limit | RIVER ALN |  |  | Commissioned in 2019 - full year data expected | 99.8078 | 21 | 99.98%
Northumbrian Water | STILLINGTON OLD WORKS CSO ST004 | 6NW800396 | 254/1844 | 254/1844 |  | SO on sewer network | NZ3742623105 | GB103025072360 | Billingham Beck from Bishopton Bck to Brierle | BISHOPTON BECK |  |  | Commissioned pre-2016 - full year data expected | 58 | 31 | 99.93%
Northumbrian Water | STOBS FORD SPS | 6NW800521 | 225/G/0400 | 225/G/0400 | A1 | Storm discharge at pumping station | NZ2082986405 | GB103022077061 | Wansbeck from Font to Bothal Burn | RIVER WANSBECK |  |  | Commissioned in 2019 - full year data expected | 391.7697 | 66 | 100%
Northumbrian Water | STOCKTON ROAD CSO (SE 024) | 6NW801459 | 254/1820 | 254/1820 |  | SO on sewer network | NZ3624028116 | GB103025072410 | Billingham Beck from Source to Bishopton Beck | SHOTTON BECK |  |  | Commissioned pre-2016 - full year data expected | 32.5 | 24 | 99.97%
Northumbrian Water | STOKESLEY PUMPING STATION NO 1 SSO | 6NW800662 | 254/C/0427 | 254/C/0427 |  | Storm discharge at pumping station | NZ5230008400 | GB103025071890 | Leven from Source to Tame | LEVEN |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | STOKESLEY SPS NO 2 CSO | 6NW800663 | 254/C/0428 | 254/C/0428 | A1 | Storm discharge at pumping station | NZ5261208446 | GB103025071890 | Leven from Source to Tame | RIVER LEVEN |  |  | Commissioned in 2019 - full year data expected | 192.8222 | 36 | 99.88%
Northumbrian Water | STOKESLEY SEWAGE TREATMENT WORKS | 6NW800799 | 25/04/1656 | 25/04/1656 | A3 | Storm tank at WwTW | NZ5221807752 | GB103025071870 | Broughton Beck from Source to River Leven | RIVER LEVEN |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | STONEBRIDGE SEWAGE PUMPING STATION | 6NW801199 | 244/0491 | 244/0491 |  | Storm discharge at pumping station | NZ2577041500 | GB103024077551 | Browney from Smallhope Burn Deerness confl | BROWNEY |  |  | Commissioned in 2020 - full year data expected | 282.2858 | 51 | 90.45%
Northumbrian Water | STONEBRIDGE SEWAGE PUMPING STATION | 6NW800531 | 244/0491 | 244/0491 | A1 | Storm discharge at pumping station | NZ2577041500 | GB103024077551 | Browney from Smallhope Burn Deerness confl | BROWNEY |  |  | Commissioned pre-2016 - full year data expected | 86.5 | 40 | 99.98%
Northumbrian Water | STONEY LANE CSO | 6NW800346 | 235/1928 | 235/1928 |  | SO on sewer network | NZ3016555728 | 9 | #N/A | OXCLOSE BURN |  |  | Commissioned in 2017 - full year data expected | 3 | 6 | 99.99%
Northumbrian Water | STONEY RIGG | 6NW801627 | 232/1178 | 232/1178 |  | SO on sewer network | NY7010063560 | GB103023075532 | South Tyne from Tipalt Burn to Allen | SOUTH TYNE |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | STONY ROW CSO | 6NW801162 | 235/1532 | 235/1532 |  | SO on sewer network | NZ2340054100 | GB103023075670 | Team from Source to Tyne | URPETH BURN |  |  | Commissioned pre-2016 - full year data expected | 59 | 40 | 99.95%
Northumbrian Water | STOREY PARK CSO | 6NW000011 | 225/1077 | 225/1077 |  | SO on sewer network | NZ1978085200 | GB103022077061 | Wansbeck from Font to Bothal Burn | CHURCH BURN |  |  | Commissioned in 2016 - full year data expected | 0.25 | 1 | 99.61%
Northumbrian Water | STOTSFIELD BURN CSO | 6NW800226 | 241/1050 | 241/1050 |  | SO on sewer network | NY9416042159 | GB103024077530 | Rookhope Burn from Source to Wear | ROOKHOPE BURN |  |  | Commissioned in 2017 - full year data expected | 146 | 11 | 62.59% | Access - Unable to retrieve data from non-telemetry data logger (NB: not to be used for delayed access to fix existing fault) | Scheduled
Northumbrian Water | STRAIT LANE CSO | 6NW801378 | 254/1806 | 254/1806 |  | SO on sewer network | NZ3100010000 | GB103025072595 | Tees from Skerne to Tidal Limit | TEES |  |  | Commissioned pre-2016 - full year data expected | 74.5 | 21 | 99.98%
Northumbrian Water | NEASHAM ROAD PUMPING STATION STRAIT LANE STRAWBERRY COTTAGE | 6NW801673 | 254/1017 | Permit Anomaly - EO Permit 254/1017 | To be permitted for storm | Storm discharge at pumping station | NZ3133110087 | GB103025072595 | Tees from Skerne to Tidal Limit | River Tees |  |  | Commissioned pre-2016 - full year data expected | 238.75 | 29 | 94.22%
Northumbrian Water | STRESSHOLME STW | 6NW800769 | 25/04/1797 | 25/04/1797 | 25/04/1797-04 | Storm tank at WwTW | NZ2873010160 | GB103025072190 | Tees from River Greta to River Skerne | TEES |  |  | Feb 2021 | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | SUMMERHILL CSO | 6NW800253 | 233/1227 | 233/1227 |  | SO on sewer network | NZ1809563602 | GB103023074791 | Blaydon Burn | RIVER TYNE SALINE ESTUARY |  |  | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
Northumbrian Water | SUNN INN CSO | 6NW801096 | 225/1059 | 225/1059 |  | SO on sewer network | NZ1982685238 | GB103022077061 | Wansbeck from Font to Bothal Burn | CHURCH BURN |  |  | Commissioned pre-2016 - full year data expected | 42.25 | 18 | 99.57%
Northumbrian Water | SUNDERLAND BRIDGE CSO | 6NW801226 | 243/D/0368 | 243/D/0368 |  | SO on sewer network | NZ2654837751 | GB103024077464 | Wear from Gaunless to Browney | RIVER WEAR |  |  | Commissioned pre-2016 - full year data expected | 321 | 70 | 98.72% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution
Northumbrian Water | SUNDERLAND BRIDGE STW | 6NW800761 | 243/0976 | 243/0976 | 243/0976-04 | Storm tank at WwTW | NZ2634037600 | GB103024077464 | Wear from Gaunless to Browney | RIVER WEAR |  |  | Commissioned in 2020 - full year data expected | 1705.5706 | 117 | 100%
Northumbrian Water | BARLEY MOW PARK CSO | 6NW000012 | EPRCB3191AV | EPRCB3191AV |  | SO on sewer network | NZ4001955825 | GB103024077640 | Hendon Coastal Area | HENDON BURN |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 48.05% | Comms failure / issue | Scheduled
Northumbrian Water | SUNDERLAND ROAD CSO | 6NW800415 | 255/1222 | 255/1222 |  | SO on sewer network | NZ4391443354 | 367 | #N/A | HORDEN BURN |  |  | Commissioned pre-2016 - full year data expected | 50.75 | 24 | 81.82% | Comms failure / issue | Scheduled
Northumbrian Water | SUNDIAL PLACE CSO | 6NW801481 | 25/04/1604 | 25/04/1604 |  | SO on sewer network | NZ3614621382 | GB103025072280 | Bishopton Beck from Source to Billingham Beck | BISHOPTON BECK |  |  | Commissioned pre-2016 - full year data expected | 6.25 | 11 | 85.39% | Comms failure / issue | Resolved - November
Northumbrian Water | SUNNISIDE CSO | 6NW801115 | EPRBB3498WT | EPRBB3498WT |  | SO on sewer network | NZ2081458715 | GB103023075670 | Team from Source to Tyne | CULVERTED SECTION BLACK BURN |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 96.86%
Northumbrian Water | SUNNYBROW SEWAGE PUMPING STATION | 6NW801078 | 243/D/0395 | 243/D/0395 | A1 | Storm discharge at pumping station | NZ1972033898 | GB103024077464 | Wear from Gaunless to Browney | HOLY WELL BURN |  |  | Commissioned pre-2016 - full year data expected | 740 | 73 | 99.21% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | SWADDLES HOLE CSO | 6NW801485 | 235/1915 | 235/1915 |  | SO on sewer network | NZ3642068490 | GB510302310200 | TYNE | RIVER TYNE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.74%
Northumbrian Water | SWAINBY STW Storm Tank | 6NW800795 | 254/1962 | 254/1962 | 254/1962-03 | Storm tank at WwTW | NZ4778002900 | GB103025071850 | Potto Beck Catchment (trib of Leven) | POTTO BECK |  |  | Commissioned in 2019 - full year data expected | 228.1775 | 17 | 99.99%
Northumbrian Water | SWARLAND FENCE PUMPING STATION | 6NW800461 | 223/0839 | 223/0839 | A | Storm discharge at pumping station | NU1568001260 | GB103022076660 | Swarland Burn Catchment (trib of Coquet) | FENCE BURN |  |  | Commissioned in 2020 - full year data expected | 808.6922 | 96 | 99.05%
Northumbrian Water | SWARLAND OLD SEWAGE WORKS CSO | 6NW800851 | 223/0947 | 223/0947 |  | SO on sewer network | NU1707003330 | GB103022076693 | Coquet from Forest Burn to Tidal Limit | MERE BURN |  |  | Commissioned pre-2016 - full year data expected | 207.5 | 29 | 99.87%
Northumbrian Water | SWINBURNE STREET CSO | 6NW800317 | 235/1925 | 235/1925 |  | SO on sewer network | NZ2526963670 | GB510302310200 | TYNE | RIVER TYNE |  |  | Commissioned in 2018 - full year data expected | 192.4689 | 73 | 100%
Northumbrian Water | SWINBURN PLACE CSO | 6NW801285 | 235/1967 | 235/1967 |  | SO on sewer network | NZ2648055680 | GB103023075670 | Team from Source to Tyne | ROWLETCH BURN |  |  | Commissioned pre-2016 - full year data expected | 1 | 1 | 99.99%
Northumbrian Water | TAME BRIDGE PS | 6NW800653 | 25/04/1692 | 25/04/1692 | 25/04/1692-01 | Storm discharge at pumping station | NZ5123008230 | GB103025071910 | Tame from Source to Leven | RIVER TAME |  |  | Commissioned pre-2016 - full year data expected | 332 | 25 | 99.94%
Northumbrian Water | TANFIELD COMPREHENSIVE SCHOOL CSO | 6NW800263 | 235/1716 | 235/1716 |  | SO on sewer network | NZ1918053780 | GB103023075670 | Team from Source to Tyne | KYO BURN |  |  | Commissioned pre-2016 - full year data expected | 10.5 | 11 | 99.83%
Northumbrian Water | TANFIELD TRUNK SEWER CSO | 6NW800250 | 235/1931 | 235/1931 |  | SO on sewer network | NZ1714352689 | GB103023075670 | Team from Source to Tyne | KYO BURN (RIVER TEAM) |  |  | Commissioned pre-2016 - full year data expected | 81.5 | 23 | 99.93%
Northumbrian Water | TANNERS ROAD CSO TD028 | 6NW800896 | 233/1238 | 233/1238 |  | SO on sewer network | NY9331264296 | GB103023075801 | Tyne from Watersmeet to Tidal Limit | COCKSHAW BURN |  |  | Commissioned pre-2016 - full year data expected | 0.76667 | 6 | 83.3% | Comms failure / issue | Resolved - July
Northumbrian Water | TANTON ROAD CSO | 6NW801590 | 25/04/1629 | 25/04/1629 |  | SO on sewer network | NZ5267009610 | GB103025071910 | Tame from Source to Leven | MEADOWFIELD STELL |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | TAY STREET CSO | 6NW800984 | 234/1160 | 234/1160 |  | SO on sewer network | NZ1242358329 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | TRIB OF RIVER DERWENT |  |  | Commissioned pre-2016 - full year data expected | 9 | 10 | 99.99%
Northumbrian Water | BRIARDALE ROAD CSO TAYLOR STREET | 6NW801349 | 226/1050 | 226/1050 |  | SO on sewer network | NZ2906281980 | GB510302203200 | BLYTH (N) | BLYTH ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 107.5 | 41 | 99.99%
Northumbrian Water | TEAMS CSO JOHNSON STREET E17-105 | 6NW800305M5 | EPRBB3893EZ | EPRBB3893EZ |  | SO on sewer network | NZ2417262805 | 8 | #N/A | RIVER TYNE |  |  | Commissioned in 2020 - full year data expected | 276.5989 | 40 | 98.04%
Northumbrian Water | TEDDER AVENUE SSO | 6NW801556 | 254/E/0431 | 254/E/0431 |  | SO on sewer network | NZ4640015800 | GB103025072180 | Stainsby Beck Catchment (trib of Tidal Tees) | STAINSBY BECK |  |  | Commissioned pre-2016 - full year data expected | 3.25 | 6 | 99.99%
Northumbrian Water | TEES DOCK ROAD CSO | 6NW801597 | 254/1935 | 254/1935 |  | SO on sewer network | NZ5536122142 | 10 | #N/A | KINKERDALE BECK |  |  | Commissioned pre-2016 - full year data expected | 228 | 40 | 98.25%
Northumbrian Water | TEESBANK AVENUE CSO | 6NW801527 | 254/0663 | 254/0663 |  | SO on sewer network | NZ4286715217 | GB103025072595 | Tees from Skerne to Tidal Limit | TEES |  |  | Commissioned pre-2016 - full year data expected | 175.4 | 43 | 96.35%
Northumbrian Water | TEESDALE AVENUE CSO | 6NW801562 | 254/1836 | 254/1836 |  | SO on sewer network | NZ4522122938 | GB103025076010 | Billingham Beck from Brierley Beck to Tees Es | BILLINGHAM BECK |  |  | Commissioned pre-2016 - full year data expected | 26.5 | 17 | 99.99%
Northumbrian Water | TEESSIDE HIGH SCHOOL PS | 6NW800624 | 254/1431 | QC.25/04/1431 | A | Storm discharge at pumping station | NZ4276714969 | GB103025072595 | Tees from Skerne to Tidal Limit | River Tees |  |  | Commissioned in 2020 - full year data expected | 2.9978 | 16 | 98.81%
Northumbrian Water | TEMPLE HOUSE PS | 6NW801628 | 232/1141 | 232/1141 | 232/1141-01 | Storm discharge at pumping station | NY8456064530 | GB103023075710 | South Tyne from Allen to North Tyne | LANGLEY BURN |  |  | Commissioned pre-2016 - full year data expected | 451 | 38 | 88.6% | Comms failure / issue | Resolved - July
Northumbrian Water | TEMPLE STREET CSO | 6NW800381 | 235/1943 | 235/1943 |  | SO on sewer network | NZ3534566008 | GB510302310200 | TYNE | RIVER TYNE ESTUARINE WATERS |  |  | Commissioned in 2018 - full year data expected | 235.2519 | 52 | 100%
Northumbrian Water | TEN ACRE FARM COMBINED SEWER OVERFL | 6NW801418 | 226/1251 | 226/1251 |  | SO on sewer network | NZ3227073170 | GB103022076180 | Brierdene Burn from Source to North Sea | BRIERDENE BURN |  |  | Commissioned pre-2016 - full year data expected | 81 | 12 | 99.08%
Northumbrian Water | STAINDROP SSO THE BLACK SWAN | 6NW800987 | 25/02/1100 | 25/02/1100 |  | SO on sewer network | NZ1331020620 | GB103025072310 | Langley Beck from Source to Sudburn Beck | LANGLEY BECK |  |  | Commissioned pre-2016 - full year data expected | 0.25 | 1 | 61.23% | Comms failure / issue | Resolved - May
Northumbrian Water | THE BOATHOUSE SPS | 6NW800509 | 235/1729 | 235/1729 | A1 | Storm discharge at pumping station | NZ1640065260 | GB510302310200 | TYNE | RIVER TYNE SALINE ESTUARY |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | THE BROOMS NORTH CSO | 6NW801206 | 235/1843 | 235/1843 |  | SO on sewer network | NZ2548054880 | GB103023075670 | Team from Source to Tyne | TRIB ROWLETCH BURN |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 94.16%
Northumbrian Water | THE CARAVAN PARK CSO | 6NW800878 | 232/1153 | 232/1153 |  | SO on sewer network | NY7164846704 | GB103023075420 | Nent from Source to South Tyne | RIVER NENT |  |  | Commissioned pre-2016 - full year data expected | 199.25 | 71 | 99.46% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution
Northumbrian Water | MARGROVE PARK CSO THE CARRS TILERY LANE | 6NW800441 | 25/06/1027 | 25/06/1027 |  | SO on sewer network | NZ6486015980 | GB103025071970 | Skelton Beck Catch (Saltburn) trib of North Sea | LITTLE BECK TRIB |  |  | Commissioned in 2020 - full year data expected | 0 | 0 | 15.17% | Comms failure / issue | N/A - Ongoing investigation
Northumbrian Water | FALLOWS CSO | 6NW800972 | 242/1063 | 242/1063 |  | SO on sewer network | NZ1291024130 | GB103024072690 | Gaunless from Source to Hummer Beck | BLACK BURN, TRIBUTARY OF |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 38.68% | Comms failure / issue | Scheduled
Northumbrian Water | THE FIRS CSO ED003 | 6NW800881 | 232/1167 | 232/1167 |  | SO on sewer network | NY7165346139 | GB103023075531 | South Tyne from Black Burn to Tipalt Burn | RIVER SOUTH TYNE |  |  | Commissioned pre-2016 - full year data expected | 0.75 | 2 | 30.61% | Comms failure / issue | N/A - Ongoing investigation
Northumbrian Water | THE GABLES CSO | 6NW801191 | 224/0955 | 224/0955 |  | SO on sewer network | NZ2604093470 | 362 | #N/A | HOUNDALEE LETCH |  |  | Commissioned pre-2016 - full year data expected | 3.75 | 3 | 99.99%
Northumbrian Water | THE GREEN COMBINED SEWER OVERFLOW | 6NW801564 | 25/04/1605 | 25/04/1605 |  | SO on sewer network | NZ4557832216 | GB103025076030 | Greatham Beck Catchment (trib of Tidal Tees) | UNNAMED TRIBUTARY OF CHAR BECK |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 66.06% | Sensor failure / issue | Resolved - August
Northumbrian Water | THE GREEN MARKET CSO | 6NW800314 | 235/1484 | 235/1484 |  | SO on sewer network | NZ2450060481 | GB103023075670 | Team from Source to Tyne | RIVER TEAM |  |  | Commissioned in 2019 - full year data expected | 318.5 | 65 | 99.95%
Northumbrian Water | THE HAGG CSO | 6NW800920 | 251/0862 | 251/0862 |  | SO on sewer network | NZ0110219888 | GB103025072240 | Balder Catchment (trib of Tees) | TRIB OF RIVER BALDER |  |  | Commissioned pre-2016 - full year data expected | 9.9669 | 9 | 32.41% | Comms failure / issue | Scheduled | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: Cost beneficial outcome not yet determined
Northumbrian Water | THE HOLLOWS CSO WV49 | 6NW801017 | 241/1108 | 241/1108 |  | SO on sewer network | NZ1631533963 | GB103024077390 | Beechburn Beck (Trib of Wear) | BEECHBURN BECK |  |  | Commissioned pre-2016 - full year data expected | 107.5 | 36 | 98.33%
Northumbrian Water | THE HOLLOWS CSO WV50 | 6NW800243 | 241/1125 | 241/1125 |  | SO on sewer network | NZ1641434186 | GB103024077390 | Beechburn Beck (Trib of Wear) | BEECHBURN BECK |  |  | Commissioned pre-2016 - full year data expected | #N/A | #N/A | 0% | Comms failure / issue | Scheduled | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | THE LENDINGS (STARTFORTH) SPS | 6NW800923 | 252/0993 | 252/0993 | A (Storm Sewage) | Storm discharge at pumping station | NZ0499415948 | GB103025072512 | Tees from Percy Beck to River Greta | RIVER TEES |  |  | Commissioned pre-2016 - full year data expected | 65 | 15 | 99.79%
Northumbrian Water | THE MEADOWS CSO (SE 022) | 6NW801458 | 254/1819 | 254/1819 |  | SO on sewer network | NZ3566528224 | GB103025072410 | Billingham Beck from Source to Bishopton Beck | UNNAMED TRIB OF SHOTTON BECK |  |  | Commissioned pre-2016 - full year data expected | 6.25 | 9 | 99.93%
Northumbrian Water | BOURNMOOR SPS | 6NW800572 | 245/1329 | 245/1329 | A1 | Storm discharge at pumping station | NZ3065050950 | GB103024077570 | Lumley Park Burn from Herrington Burn to R Wear | LUMLEY PARK BURN |  |  | Commissioned in 2020 - full year data expected | 3.95 | 8 | 100%
Northumbrian Water | THE MIDDLES CSO | 6NW801111 | 245/1148 | 245/1148 |  | SO on sewer network | NZ2073351684 | GB103024077590 | Twizell Burn from Source to Cong Burn | STANLEY BURN TRIB |  |  | Commissioned pre-2016 - full year data expected | 322.2658 | 91 | 93.73% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | NEW ROAD CSO | 6NW801565 | 25/04/1711 | 25/04/1711 |  | SO on sewer network | NZ4614021420 | 10 | #N/A | MILL RACE |  |  | Commissioned pre-2016 - full year data expected | 0.25 | 1 | 93.23%
Northumbrian Water | OLD SCHOOL COMBINED SEWER OVERFLOW | 6NW800903 | 25/01/0916 | 25/01/0916 |  | SO on sewer network | NY9741023950 | GB103025072511 | Tees from Maize Beck to Percy Beck | HEUGH SIKE |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 97.88%
Northumbrian Water | THE OVAL CSO | 6NW801207 | 235/1839 | 235/1839 |  | SO on sewer network | NZ2547054860 | GB103023075670 | Team from Source to Tyne | TRIB ROWLETCH BURN |  |  | Commissioned pre-2016 - full year data expected | 1.5 | 1 | 99.21%
Northumbrian Water | THE OVAL PUMPING STATION | 6NW800547 | 235/1764 | 235/1764 | 235/1764-01 | Storm discharge at pumping station | NZ2792063380 | GB510302310200 | TYNE | RIVER TYNE SALINE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 1.75 | 3 | 99.99%
Northumbrian Water | THE PETH CSO | 6NW800885 | 232/1013 | 232/1013 |  | SO on sewer network | NY8351955801 | GB103023074710 | Allen from Source to West Allen | RIVER EAST ALLEN |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.84%
Northumbrian Water | THE SLACK CSO (TE 010) | 6NW800235 | 242/1064 | 242/1064 |  | SO on sewer network | NZ1131425356 | GB103024072690 | Gaunless from Source to Hummer Beck | RIVER GAUNLESS |  |  | Commissioned in 2019 - full year data expected | 0 | 0 | 64.97% | Access - Unable to retrieve data from non-telemetry data logger (NB: not to be used for delayed access to fix existing fault) | Scheduled
Northumbrian Water | THE SLACK | 6NW800236 | 242/1069 | 242/1069 |  | SO on sewer network | NZ1129025400 | GB103024072690 | Gaunless from Source to Hummer Beck | GREWBURN BECK |  |  | Commissioned in 2019 - full year data expected | 32.5 | 14 | 66.15% | Access - Unable to retrieve data from non-telemetry data logger (NB: not to be used for delayed access to fix existing fault) | Scheduled
Northumbrian Water | THE STRAY STORM RETENTION TANK | 6NW801616 | 25/06/1016 | 25/06/1016 |  | SO on sewer network | NZ6367022940 | GB650301500005 | Tees Coastal | NORTH SEA |  | Marske | Commissioned pre-2016 - full year data expected | 88.4667 | 11 | 100%
Northumbrian Water | THE SWIRLE CSO | 6NW800320 | 235/1918 | 235/1918 |  | SO on sewer network | NZ2579864071 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | Commissioned in 2018 - full year data expected | 72.1503 | 41 | 100%
Northumbrian Water | THE OLD VICARAGE CSO | 6NW800888 | 232/1140 | 232/1140 |  | SO on sewer network | NY8439264454 | GB103023075710 | South Tyne from Allen to North Tyne | RIVER SOUTH TYNE |  |  | Commissioned pre-2016 - full year data expected | 360 | 49 | 99.53% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution
Northumbrian Water | YARKER LANE CSO | 6NW800905 | 25/01/0917 | 25/01/0917 |  | SO on sewer network | NY9740123950 | GB103025072511 | Tees from Maize Beck to Percy Beck | HEUGH SIKE |  |  | Commissioned pre-2016 - full year data expected | 12 | 14 | 96%
Northumbrian Water | THORNTON STREET PS | 6NW801583 | 25/04/1769 | 25/04/1769 |  | SO on sewer network | NZ5152019780 | 10 | #N/A | MIDDLE BECK (TEES CATCHMENT) |  |  | Commissioned pre-2016 - full year data expected | 2 | 6 | 99.99%
Northumbrian Water | THORPE STREET SPS | 6NW800661 | 255/5022 | QC.25/05/5022 | A1 | Storm discharge at pumping station | NZ5216634794 | GB650301500005 | Tees Coastal | NORTH SEA |  |  | Commissioned in 2019 - full year data expected | 1035.6683 | 90 | 100%
Northumbrian Water | THORPE THEWLES SPS | 6NW800616 | 254/0974 | 254/0974 | A1 | Storm discharge at pumping station | NZ4006423218 | GB103025072360 | Billingham Beck from Bishopton Bck to Brierle | THORPE BECK (BILLINGHAM BECK) |  |  | Commissioned in 2019 - full year data expected | 198.6428 | 36 | 99.98%
Northumbrian Water | THROPTON & SNITTER STW | 6NW800697 | 223/0943 | 223/0943 | A2 | Storm tank at WwTW | NU0279102734 | GB103022076601 | Wreigh Burn from Netherton Burn to Coquet | WREIGH BURN |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | THROPTON CSO | 6NW800212 | 223/0980 | 223/0980 | A1 | Storm discharge at pumping station | NU0304002241 | GB103022076601 | Wreigh Burn from Netherton Burn to Coquet | WREIGH BURN |  |  | Commissioned in 2020 - full year data expected | 19.3881 | 6 | 37.47% | Comms failure / issue | Resolved - December
Northumbrian Water | THROSTLES NEST STORAGE TANK | 6NW800402 | 255/1192 | 255/1192 |  | SO on sewer network | NZ3945039900 | GB103025075930 | Castle Eden Burn from Source to North Sea | GORE BURN |  |  | Commissioned pre-2016 - full year data expected | 3.5 | 3 | 99.96%
Northumbrian Water | THROSTLES NEST PUMPING STATION | 6NW800612 | 255/1203 | 255/1203 | 255/1203-01 | Storm discharge at pumping station | NZ3942039830 | GB103025075930 | Castle Eden Burn from Source to North Sea | GORE BURN |  |  | Commissioned in 2020 - full year data expected | 0.40167 | 9 | 100%
Northumbrian Water | TILERY FARM STRAGE TANK CSO | 6NW800403 | 255/1185 | 255/1185 |  | SO on sewer network | NZ4088536801 | GB103025075910 | Crimdon Beck from Source to Sea | HEADS HOPE BURN |  |  | Commissioned pre-2016 - full year data expected | 648.75 | 75 | 99.21% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | TILERY STORM SEWAGE PUMPING STATION | 6NW800632 | 254/1822 | 254/1822 |  | SO on sewer network | NZ4510020400 | GB103025072550 | Lustrum Beck Catchment (trib of Tees) | LUSTRUM BECK |  |  | Commissioned in 2020 - full year data expected | 232.6872 | 62 | 99.96%
Northumbrian Water | TINDALE STW | 6NW800123 | 232/1147 | 232/1147 | 232/1147-02 | Inlet SO at WwTW | NY6196059260 | GB103023075470 | Hartley Burn from Source to Black Burn | TARN BECK |  |  | Commissioned in 2020 - full year data expected | 84.415 | 18 | 100%
Northumbrian Water | TOAD POOL CSO TE351 | 6NW801042 | 242/1049 | 242/1049 |  | SO on sewer network | NZ1742726558 | GB103024072690 | Gaunless from Source to Hummer Beck | GAUNLESS |  |  | Commissioned pre-2016 - full year data expected | 2.25 | 7 | 98.48%
Northumbrian Water | TOFT HILL EJECTOR CSO | 6NW801004 | 242/1050 | 242/1050 | A1 | Storm discharge at pumping station | NZ1543028010 | GB103024072690 | Gaunless from Source to Hummer Beck | NORTON FINE GILL, TRIBUTARY OF |  |  | Commissioned pre-2016 - full year data expected | 139.5 | 31 | 99.63%
Northumbrian Water | TOGSTON SEWAGE TREATMENT WORKS | 6NW800120 | 224/0992 | 224/0992 | 224/0992-03 | Inlet SO at WwTW | NU2501001480 | 362 | #N/A | LADY BURN |  |  | Commissioned in 2020 - full year data expected | 1395.8656 | 130 | 100%
Northumbrian Water | TOLL HOUSE ROAD CSO | 6NW801200 | 244/1001 | 244/1001 |  | SO on sewer network | NZ2557142518 | GB103024077551 | Browney from Smallhope Burn Deerness confl | RIVER BROWNEY |  |  | Commissioned pre-2016 - full year data expected | 84.5 | 51 | 98.15% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | CSO IN TOLLESBY LANE | 6NW801579 | 25/04/1665 | 25/04/1665 |  | SO on sewer network | NZ5121015060 | GB103025072210 | Marton West Beck Catchment (trib of Tidal Tees) | MARTON WEST BECK |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 100%
Northumbrian Water | TOLLESBY MANOR SPS & CSO | 6NW800655 | 254/1894 | 254/1894 | A1 | Storm discharge at pumping station | NZ5133915081 | GB103025072210 | Marton West Beck Catchment (trib of Tidal Tees) | TRIB OF MARTON WEST BECK |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.87%
Northumbrian Water | TOOL HIRE CSO | 6NW801082 | 244/0996 | 244/0996 |  | SO on sewer network | NZ1944042110 | GB103024077290 | Hedleyhope Burn from Source to Deerness | PRIEST BURN |  |  | Commissioned pre-2016 - full year data expected | 125.75 | 38 | 99.95%
Northumbrian Water | TOW LAW STW CSO INLET | 6NW800961 | 241/1106 | 241/1106 | 241/1106-04 | Inlet SO at WwTW | NZ1135638567 | GB103024077450 | Houselop Beck from Source to Wear | HOUSELOP BECK, TRIBUTARY OF |  |  | Commissioned pre-2016 - full year data expected | 375.25 | 78 | 95.21% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution
Northumbrian Water | TOW LAW STW Storm Tank | 6NW800720 | 241/1106 | 241/1106 | 241/1106-03 | Storm tank at WwTW | NZ1135638567 | GB103024077450 | Houselop Beck from Source to Wear | HOUSELOP BECK, TRIBUTARY OF |  |  | Commissioned in 2020 - full year data expected | 204.6419 | 82 | 99.8%
Northumbrian Water | TOWER STREET CSO M2 | 6NW540106M2 | 25/04/1700 | 25/04/1700 | A2 | SO on sewer network | NZ4649319169 | GB510302509900 | TEES | RIVER TEES |  |  | Commissioned pre-2016 - full year data expected | 1.7 | 6 | 100%
Northumbrian Water | TOWER STREET CSO M2 | 6NW540106M4 | 25/04/1700 | 25/04/1700 | A1 | SO on sewer network | NZ4649319169 | GB510302509900 | TEES | RIVER TEES |  |  | Commissioned in 2017 - full year data expected | 0 | 0 | 100%
Northumbrian Water | TRAVELLERS GREEN CSO (SE015) | 6NW801301 | 253/1263 | 253/1263 |  | SO on sewer network | NZ2910823663 | GB103025072391 | Skerne form Woodham Burn to Demons Beck | RIVER SKERNE |  |  | Commissioned pre-2016 - full year data expected | 138.5 | 63 | 99.57% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: Cost beneficial outcome not yet determined
Northumbrian Water | TRIMDON COLLIERY SPS | 6NW800606 | 25/03/1233 | 25/03/1233 | A1 | Storm discharge at pumping station | NZ3815235365 | GB103025076070 | Skerne from Source to Carrs | LANGLEY BECK |  |  | Commissioned in 2019 - full year data expected | 456.2694 | 72 | 99.99%
Northumbrian Water | TRIMDON VILLAGE SEWAGE TREATMENT WO CSO INLET | 6NW800184 | 25/03/1232 | 25/03/1232 | 25/03/1232-03 | Inlet SO at WwTW | NZ3766034510 | GB103025076070 | Skerne from Source to Carrs | RIVER SKERNE |  |  | Feb 2021 | 348.1364 | 31 | 100%
Northumbrian Water | TRIMDON VILLAGE SEWAGE TREATMENT WO CSO INLET | 6NW800788 | 25/03/1232 | 25/03/1232 | 25/03/1232-02 | Storm tank at WwTW | NZ3766034510 | GB103025076070 | Skerne from Source to Carrs | RIVER SKERNE |  |  | Commissioned in 2020 - full year data expected | 924.2244 | 69 | 99.88%
Northumbrian Water | TUART STREET CSO (NO1) | 6NW801669 | #TBC | Permit Anomaly | To be permitted for storm | SO on sewer network | NZ2745551598/NZ2743851611 | GB103024077600 | Cong Burn from Twizell Burn to Wear | Culverted water course to Chester Burn |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.98%
Northumbrian Water | TUDHOE MILL SEWAGE TREATMENT WORKS CSO INLET | 6NW800164 | 243/0985 | 243/0985 | A3 | Inlet SO at WwTW | NZ2422735898 | GB103024077464 | Wear from Gaunless to Browney | VALLEY BURN |  |  | Commissioned in 2019 - full year data expected | 232.3294 | 65 | 100%
Northumbrian Water | TUDHOE MILL SEWAGE TREATMENT WORKS CSO INLET | 6NW800759 | 243/0985 | 243/0985 | A2 | Storm tank at WwTW | NZ2422735898 | GB103024077464 | Wear from Gaunless to Browney | VALLEY BURN |  |  | Commissioned in 2019 - full year data expected | 896.1583 | 82 | 100%
Northumbrian Water | TUDOR CROFT COTTAGE CSO L017 | 6NW801607 | 256/1043 | 256/1043 |  | SO on sewer network | NZ6003915452 | GB103025071970 | Skelton Beck Catch (Saltburn) trib of North Sea | HUTTON BECK |  |  | Commissioned pre-2016 - full year data expected | 302.75 | 57 | 99.94%
Northumbrian Water | TUDOR ROAD CSO | 6NW800389 | 235/1905 | 235/1905 |  | SO on sewer network | NZ3583766907 | 8 | #N/A | RIVER TYNE ESTUARINE WATERS |  |  | Commissioned in 2018 - full year data expected | 80.3783 | 37 | 91.76%
Northumbrian Water | TURNBERRY WAY CSO | 6NW801214 | 235/1964 | 235/1964 |  | SO on sewer network | NZ2549668514 | GB103023075780 | Ouse Burn from Source to Tyne | OUSE BURN |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.98%
Northumbrian Water | TURNER STREET SPS | 6NW800871 | 223/0950 | 223/0950 |  | SO on sewer network | NU2649204607 | GB510302203000 | COQUET | RIVER COQUET (SALINE ESTUARY) |  | Warkworth & Amble Links | Commissioned pre-2016 - full year data expected | 169.3333 | 60 | 99.92%
Northumbrian Water | TUTHILL STAIRS CSO | 6NW800310 | 235/1922 | 235/1922 |  | SO on sewer network | NZ2502063650 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 80.09% | Sensor failure / issue | N/A - Ongoing investigation
Northumbrian Water | TWEEDSIDE INDUSTRIAL ESTATE CSO | 6NW800818 | 210/1335 | 210/1335 |  | SO on sewer network | NT9962652518 | GB510202110000 | TWEED | RIVER TWEED (SALINE ESTUARY) |  | Spittal | Commissioned pre-2016 - full year data expected | 55.2667 | 35 | 100%
Northumbrian Water | TYNE GREEN CSO TD030 | 6NW800897 | 233/1239 | 233/1239 |  | SO on sewer network | NY9349264832 | GB103023075801 | Tyne from Watersmeet to Tidal Limit | COCKSHAW BURN |  |  | Commissioned pre-2016 - full year data expected | 2.3 | 7 | 100%
Northumbrian Water | TYNE STREET SPS | 6NW801436 | 235/1656 | 235/1656 | A1 | Storm discharge at pumping station | NZ3305065810 | 8 | #N/A | TYNE SALINE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 0.25 | 1 | 99.86%
Northumbrian Water | TYNE VIEW CSO | 6NW800205 | 233/0991 | 233/0991 |  | SO on sewer network | NZ1849264426 | GB510302310200 | TYNE | LEMINGTON GUT |  |  | Commissioned in 2017 - full year data expected | 243.4667 | 36 | 67.56% | Telemetry or data archiving failure / issue | Scheduled | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | TYNE VIEW TERRACE PS | 6NW800590 | 235/1690 | 235/1690 | 235/1690-01 | Storm discharge at pumping station | NZ3328066100 | GB510302310200 | TYNE | TYNE |  |  | Commissioned in 2020 - full year data expected | 486.8286 | 55 | 92.32%
Northumbrian Water | TYNESIDE CSO (NO B5/301) NEWLAND DRIVE | 6NW800370 | 235/B/0169 | 235/B/0169 |  | SO on sewer network | NZ3348164722 | GB103023075690 | Don from Source to Tidal Limit | DON |  |  | Commissioned in 2018 - full year data expected | 884.7558 | 107 | 100%
Northumbrian Water | TYNESIDE CSO B5/201 | 6NW800369 | 235/B/0168 | 235/B/0168 |  | SO on sewer network | NZ3351164888 | GB103023075690 | Don from Source to Tidal Limit | RIVER DON |  |  | Commissioned in 2020 - full year data expected | 119.7336 | 27 | 91.78%
Northumbrian Water | ULGHAM SEWAGE TREATMENT WORKS | 6NW800756 | 224/A/0887 | 224/A/0887 |  | Storm tank at WwTW | NZ2347192570 | GB103022076820 | Lyne from Source to Tidal Limit | River Lyne |  |  | Commissioned in 2020 - full year data expected | 320.6236 | 54 | 100%
Northumbrian Water | ULSWATER CRESCENT CSO | 6NW801019 | 241/1130 | 241/1130 |  | SO on sewer network | NZ1663435102 | GB103024077390 | Beechburn Beck (Trib of Wear) | CROOK BECK |  |  | Commissioned pre-2016 - full year data expected | 123 | 34 | 99.95%
Northumbrian Water | UNION QUAY CSO | 6NW800391 | EPRBB3497EZ | EPRBB3497EZ |  | SO on sewer network | NZ3614468363 | GB510302310200 | TYNE | RIVER TYNE (TIDAL) |  |  | Commissioned in 2017 - full year data expected | 5.8333 | 6 | 97.01%
Northumbrian Water | JOYCE TERRACE AND DEERNESS VIEW STW | 6NW800159 | 244/E/0315 | 244/E/0315 | 244/E/0315-01 | Inlet SO at WwTW | NZ2180042900 | GB103024077280 | Deerness from Hedleyhope Burn to Browney | River Deerness |  |  | Commissioned in 2020 - full year data expected | 4.0022 | 1 | 100%
Northumbrian Water | USWORTH HALL CSO | 6NW801393 | 235/1953 | 235/1953 |  | SO on sewer network | NZ3155058850 | GB103023075690 | Don from Source to Tidal Limit | DON, TRIBUTARY OF |  |  | Commissioned pre-2016 - full year data expected | 2.75 | 2 | 98.99%
Northumbrian Water | VALLEY TERRACE CSO | 6NW801015 | 241/1122 | 241/1122 |  | SO on sewer network | NZ1667932599 | GB103024077390 | Beechburn Beck (Trib of Wear) | BEECHBURN BECK |  |  | Commissioned pre-2016 - full year data expected | 130 | 31 | 99.2%
Northumbrian Water | VEDRA CLOSE SSO | 6NW800889 | 241/A/0999 | 241/A/0999 |  | SO on sewer network | NY8621039420 | GB103024077440 | Wear from Wearhead to Middlehope Burn, Iresho | WEAR |  |  | Commissioned pre-2016 - full year data expected | 1.25 | 2 | 99.99%
Northumbrian Water | VERONICA STREET CSO | 6NW801576 | 254/1205 | 254/1205 |  | SO on sewer network | NZ5068319719 | GB103025072210 | Marton West Beck Catchment (trib of Tidal Tees) | ORMESBY BECK |  |  | Commissioned pre-2016 - full year data expected | 73.25 | 39 | 99.81%
Northumbrian Water | VICTORIA EMBANKMENT - POLAM LANE | 6NW801296 | 25/03/1231 | 25/03/1231 |  | SO on sewer network | NZ2884413754 | GB103025072596 | Skerne from Demons Beck to Tees | RIVER SKERNE |  |  | Commissioned pre-2016 - full year data expected | 72.5 | 19 | 99.98%
Northumbrian Water | VICTORIA RD AT SANDOWN GARDENS CSO | 6NW801181 | 235/1933 | 235/1933 |  | SO on sewer network | NZ2414661344 | GB103023075670 | Team from Source to Tyne | TEAM |  |  | Commissioned pre-2016 - full year data expected | 91.75 | 35 | 90.53%
Northumbrian Water | VICTORIA ROAD CSO | 6NW800558 | 25/03/1253 | 25/03/1253 | A1 | Storm discharge at pumping station | NZ2908014160 | GB103025072596 | Skerne from Demons Beck to Tees | RIVER SKERNE |  |  | Commissioned in 2019 - full year data expected | 0.38889 | 2 | 100%
Northumbrian Water | VINDOMORA VILLAS CSO | 6NW800959 | 234/1155 | 234/1155 |  | SO on sewer network | NZ1052155764 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | BLACKSTONE BURN RIVER DERWENT |  |  | Commissioned pre-2016 - full year data expected | 19 | 17 | 99.97%
Northumbrian Water | VINOVIUM CSO A27 | 6NW801099 | 242/C/0385 | 242/C/0385 |  | SO on sewer network | NZ2101627823 | GB103024072730 | Gaunless from Hummer Beck to Wear | GAUNLESS |  |  | Commissioned pre-2016 - full year data expected | 27.75 | 29 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | VINOVIUM SSO NO A13 | 6NW801134 | 242/C/0371 | 242/C/0371 |  | SO on sewer network | NZ2150029900 | GB103024072730 | Gaunless from Hummer Beck to Wear | GAUNLESS |  |  | Commissioned pre-2016 - full year data expected | 10.5 | 14 | 99.99%
Northumbrian Water | GIB CHARE HOUSING DEVELOPMENT VINOVIUM NOA14 | 6NW801133 | 242/C/0372 | 242/C/0372 |  | SO on sewer network | NZ2140029800 | GB103024072730 | Gaunless from Hummer Beck to Wear | GAUNLESS |  |  | Commissioned pre-2016 - full year data expected | 5 | 11 | 99.83%
Northumbrian Water | VINOVIUM SSOS A17, A18, A19 & A21 | 6NW801129 | 242/C/0375 | 242/C/0375 |  | SO on sewer network | NZ2132828289 | GB103024072730 | Gaunless from Hummer Beck to Wear | River Gaunless |  |  | Commissioned pre-2016 - full year data expected | 9.25 | 18 | 99.63%
Northumbrian Water | VINOVIUM CSO NO A22 | 6NW800275 | 242/C/0380 | 242/C/0380 |  | SO on sewer network | NZ2182128532 | GB103024072730 | Gaunless from Hummer Beck to Wear | RIVER GAUNLESS |  |  | Commissioned in 2017 - full year data expected | #N/A | #N/A | 0% | Comms failure / issue | Scheduled
Northumbrian Water | VINOVIUM CSO NO A9 | 6NW801104 | 242/C/0368 | 242/C/0368 |  | SO on sewer network | NZ2065130313 | GB103024077463 | Wear from Beechburn Beck to Gaunless | RIVER WEAR |  |  | Commissioned pre-2016 - full year data expected | 0.5 | 2 | 99.99%
Northumbrian Water | VINOVIUM STW | 6NW800744 | 243/0966 | 243/0966 | 243/0966-03 | Storm tank at WwTW | NZ2044031770 | GB103024077464 | Wear from Gaunless to Browney | WEAR |  |  | Commissioned in 2020 - full year data expected | 836.1108 | 77 | 96.2%
Northumbrian Water | AVENUE VIVIAN CSO SU013 | 6NW801657 | 245/1375 | 245/1375 |  | SO on sewer network | NZ3200750504 | GB103024077580 | Lumley Park Burn from Source to Herrington Burn | MOORS BURN |  |  | Commissioned pre-2016 - full year data expected | 52.25 | 17 | 87.44% | Comms failure / issue | Resolved - November
Northumbrian Water | VULCAN STREET OUTFALL | 6NW800651 | 254/1513 | QR.25/04/1513 | A | Storm discharge at pumping station | NZ5028721138 | 10 | #N/A | River Tees |  |  | May 2021 | 1.0139 | 4 | 100%
Northumbrian Water | WADDINGTON STREET CSO | 6NW801228 | 245/1287 | 245/1287 |  | SO on sewer network | NZ2671042670 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | RIVER WEAR |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.91%
Northumbrian Water | WADES FARM CSO WV 010 | 6NW801072 | 242/1061 | 242/1061 |  | SO on sewer network | NZ1962826211 | GB103024072730 | Gaunless from Hummer Beck to Wear | RIVER GAUNLESS |  |  | Commissioned pre-2016 - full year data expected | 32 | 12 | 66.93% | Comms failure / issue | Resolved - September
Northumbrian Water | WAGONWAY ROAD PUMPING STATION | 6NW800578 | 235/1745 | 235/1745 | 235/1745-01 | Storm discharge at pumping station | NZ3152065820 | GB510302310200 | TYNE | RIVER TYNE SALINE ESTUARY |  |  | Commissioned in 2020 - full year data expected | 2390.9578 | 155 | 100%
Northumbrian Water | WALDRIDGE ROAD CSO CH 13 | 6NW801201 | 245/1305 | 245/1305 |  | SO on sewer network | NZ2528050380 | GB103024077560 | Cong Burn from Source to Twizell Burn | CONG BURN |  |  | Commissioned pre-2016 - full year data expected | 0.5 | 2 | 99.56%
Northumbrian Water | WALKERGATE DURHAM CSO | 6NW801267 | EPRCB3097WP | EPRCB3097WP |  | SO on sewer network | NZ2733142671 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | RIVER WEAR |  |  | Commissioned pre-2016 - full year data expected | 12.75 | 12 | 99.61%
Northumbrian Water | WALLRIDGE SEWAGE DISPOSAL WORKS | 6NW800807 | 226/0150 | Permit Anomaly - STW permit 226/0150 | to be permitted for settled storm | Storm tank at WwTW | NZ0590076400 | GB103022076890 | Coldcoats Burn Catchment (trib of Pont) | Cleugh Burn |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | WANSBECK ROAD CSO (NTY 007) | 6NW801216 | 226/1256 | 226/1256 |  | SO on sewer network | NZ2585173432 | GB103022076190 | Seaton Burn from Source to Tidal Limit | SEATON BURN |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | WAPPING STREET CSO | 6NW801484 | 235/1902 | 235/1902 |  | SO on sewer network | NZ3625168068 | GB510302310200 | TYNE | RIVER TYNE ESTUARINE WATERS |  |  | Commissioned pre-2016 - full year data expected | 311.75 | 44 | 98.75%
Northumbrian Water | WARDEN GROVE SSO | 6NW801423 | 245/C/0293 | 245/C/0293 |  | SO on sewer network | NZ3378448740 | GB103024077580 | Lumley Park Burn from Source to Herrington Burn | RAINTON BURN |  |  | Commissioned pre-2016 - full year data expected | 123.75 | 54 | 99.5% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | WARDEN VILLAGE STW | 6NW800891 | 231/0271 | 231/0271 | A2 | Inlet SO at WwTW | NY9169666201 | GB103023075802 | N Tyne from Barrasford to S Tyne confluence | NORTH TYNE |  |  | Commissioned pre-2016 - full year data expected | 0.25 | 1 | 99.99%
Northumbrian Water | WARK SEWAGE TREATMENT WORKS | 6NW800453 | 210/1312 | 210/1312 | 210/1312-03 | Storm discharge at pumping station | NT8275038650 | 437 | #N/A | THE GOAT |  |  | Commissioned pre-2016 - full year data expected | 181.5 | 33 | 99.3%
Northumbrian Water | WARK STW | 6NW800703 | 231/1071 | 231/1071 | 231/1071-03 | Storm tank at WwTW | NY8627076660 | GB103023074920 | N Tyne from Rede to Gunnerton Burn | RIVER NORTH TYNE |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | WARRENBY SEA OUTFALL | 6NW800670 | 256/0908 | 256/0908 | A | Storm discharge at pumping station | NZ5836025970 | GB650301500005 | Tees Coastal | NORTH SEA |  | Redcar Coatham | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
Northumbrian Water | WARSDELL STREET PUMPING STATION | 6NW801401 | 226/1154 | 226/1154 | 226/1154-01 | Storm discharge at pumping station | NZ3116082360 | GB510302203200 | BLYTH (N) | BLYTH SALINE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 3.5 | 3 | 99.99%
Northumbrian Water | WASHINGTON STW CSO INLET | 6NW800177 | 245/1244 | 245/1244 | 245/1244-04 | Inlet SO at WwTW | NZ3310055530 | GB510302402900 | WEAR | WEAR |  |  | November 2021 | 56.9906 | 7 | 100%
Northumbrian Water | WASHINGTON STW Storm Tank | 6NW800781 | 245/1244 | 245/1244 | 245/1244-03 | Storm tank at WwTW | NZ3310055530 | GB510302402900 | WEAR | WEAR |  |  | Feb 2021 | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | WASHINGTON VILLAGE CEMETRY CSO | 6NW801391 | NPSWQD006113 | NPSWQD006113 |  | SO on sewer network | NZ3183055950 | 9 | #N/A | WILLOWS POND |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.98%
Northumbrian Water | WASHINGWELL SCHOOL CSO | 6NW801139 | 235/1508 | 235/1508 |  | SO on sewer network | NZ2168660319 | GB103023075670 | Team from Source to Tyne | BLACK BURN TRIB |  |  | Commissioned pre-2016 - full year data expected | 1.75 | 2 | 95.53%
Northumbrian Water | WATERHOUSE CSO | 6NW801148 | EPRAB3691VY | EPRAB3691VY |  | SO on sewer network | NZ2268041971 | GB103024077280 | Deerness from Hedleyhope Burn to Browney | RIVER BURN |  |  | Commissioned pre-2016 - full year data expected | 1 | 2 | 99.98%
Northumbrian Water | WATERVILLE ROAD CSO | 6NW800375 | 235/1898 | 235/1898 |  | SO on sewer network | NZ3469767619 | 8 | #N/A | WEST END PARK BURN |  |  | Commissioned in 2017 - full year data expected | 0.3 | 2 | 100%
Northumbrian Water | WATTS SLOPE HIGH LEVEL CSO (A56) | 6NW800383 | 235/1796 | 235/1796 |  | SO on sewer network | NZ3547372800 | GB650301500002 | Tyne and Wear | NORTH SEA |  | Whitley Bay | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
Northumbrian Water | WEAR CHARE CSO | 6NW801136 | 241/1116 | 241/1116 |  | SO on sewer network | NZ2111030410 | GB103024077463 | Wear from Beechburn Beck to Gaunless | WEAR |  |  | Commissioned pre-2016 - full year data expected | 93.5 | 59 | 99.49% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | WEAR VIEW A CSO SE001 | 6NW801145 | 243/0992 | 243/0992 |  | SO on sewer network | NZ2208034140 | GB103024077464 | Wear from Gaunless to Browney | STRAIT THE |  |  | Commissioned pre-2016 - full year data expected | 2.25 | 6 | 99%
Northumbrian Water | WEAR VIEW B CSO | 6NW800288 | 243/0921 | 243/0921 |  | SO on sewer network | NZ2208734118 | GB103024077464 | Wear from Gaunless to Browney | THE STRAIT, CULVERTED WATERCRS |  |  | Commissioned in 2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | WELL BANK CSO TD008 | 6NW800906 | 233/1252 | 233/1252 |  | SO on sewer network | NY9866364410 | GB103023075801 | Tyne from Watersmeet to Tidal Limit | RIVER TYNE |  |  | Commissioned pre-2016 - full year data expected | 283.25 | 56 | 97.18% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | WELL BANK CSO | 6NW801300 | 25/03/1254 | 25/03/1254 |  | SO on sewer network | NZ2859722534 | GB103023075801 | Tyne from Watersmeet to Tidal Limit | RIVER SKERNE |  |  | Commissioned pre-2016 - full year data expected | 4.25 | 6 | 99.99%
Northumbrian Water | WELLFIELD PS | 6NW800617 | 255/1108 | 255/1108 | 255/1108-02 | Storm discharge at pumping station | NZ4046038485 | GB103025075930 | Castle Eden Burn from Source to North Sea | CASTLE EDEN BURN TRIB |  |  | Commissioned pre-2016 - full year data expected | 28.25 | 17 | 99.16%
Northumbrian Water | WELLINGTON LANE PUMPING STATION | 6NW800609 | 245/1211 | 245/1211 | 245/1211-01 | Storm discharge at pumping station | NZ3890158135 | GB510302402900 | WEAR | RIVER WEAR (SALINE ESTUARY) |  |  | Commissioned pre-2016 - full year data expected | 52.75 | 24 | 99.96%
Northumbrian Water | WELWYN FACTORY CSO | 6NW801293 | 226/1267 | 226/1267 |  | SO on sewer network | NZ2785783760 | GB103022076230 | Sleek Burn / Hepscott Burn Source to Tidal Limit | SLEEKBURN |  |  | Commissioned pre-2016 - full year data expected | 176.25 | 41 | 99.71%
Northumbrian Water | WESLEY TERRACE CSO | 6NW800244 | 235/1536 | 235/1536 |  | SO on sewer network | NZ1687452290 | GB103023075670 | Team from Source to Tyne | KYO BURN (CULVERTED) |  |  | Commissioned in 2016 - full year data expected | 7.25 | 10 | 99.99%
Northumbrian Water | WEST BOLDON CSO NO 3 | 6NW801467 | 235/F/0613 | 235/F/0613 |  | SO on sewer network | NZ3587062020 | GB103023075690 | Don from Source to Tidal Limit | DON |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | WEST BOLDON CSO (NO 4) | 6NW801469 | 235/F/0614 | 235/F/0614 |  | SO on sewer network | NZ3586962022 | GB103023075690 | Don from Source to Tidal Limit | DON |  |  | Commissioned pre-2016 - full year data expected | 476.75 | 79 | 99.42% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | WEST CORNFORTH SPS | 6NW800568 | 243/0979 | 243/0979 | A1 | Storm discharge at pumping station | NZ3071934663 | GB103024077410 | Croxdale Beck from Source to Wear | COXHOE BECK |  |  | Commissioned in 2016 - full year data expected | 48.75 | 26 | 99.82%
Northumbrian Water | WEST END SPS | 6NW800654 | 25/04/1596 | 25/04/1596 | A1 | Storm discharge at pumping station | NZ5195507732 | GB103025071890 | Leven from Source to Tame | RIVER LEVEN |  |  | Commissioned in 2019 - full year data expected | 370.6156 | 43 | 99.98%
Northumbrian Water | WEST HOLBORN SOUTH CSO | 6NW801473 | 235/1945 | 235/1945 |  | SO on sewer network | NZ3546666216 | GB510302310200 | TYNE | RIVER TYNE SALINE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 32.75 | 9 | 75.57% | Comms failure / issue | Scheduled
Northumbrian Water | WEST OF HEDWORTH LANE CSO | 6NW801434 | 235/C/0044 | 235/C/0044 |  | SO on sewer network | NZ3345763236 | GB103023075690 | Don from Source to Tidal Limit | DON |  |  | Commissioned pre-2016 - full year data expected | 14.25 | 21 | 99.41%
Northumbrian Water | WEST RAINTON CSO DU085 STW MH21 | 6NW800361 | 245/E/0505 | 245/E/0505 |  | SO on sewer network | NZ3011646522 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | Unnamed tributary of the River Wear |  |  | Commissioned in 2017 - full year data expected | 0 | 0 | 64.64% | Comms failure / issue | Resolved - April
Northumbrian Water | WEST RAINTON CSO DU085 STW MH21 | 6NW801388 | 245/E/0506 | 245/E/0506 |  | SO on sewer network | NZ3011646522 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | Unnamed tributary of the River Wear |  |  | Commissioned pre-2016 - full year data expected | 41.25 | 23 | 99.97%
Northumbrian Water | WEST RAINTON CSO DU085 STW MH21 | 6NW801386 | 245/E/0507 | 245/E/0507 |  | SO on sewer network | NZ3011646522 | GB103024077621 | Wear from Croxdale Beck to Lumley Park Burn | WEAR |  |  | Commissioned pre-2016 - full year data expected | 126 | 35 | 74.06% | Comms failure / issue | Resolved - October
Northumbrian Water | WEST ROAD CSO | 6NW801018 | 241/1138 | 241/1138 |  | SO on sewer network | NZ1638335029 | GB103024077390 | Beechburn Beck (Trib of Wear) | CROOK BECK, TRIBUTARY OF |  |  | Commissioned pre-2016 - full year data expected | 252 | 45 | 99.98%
Northumbrian Water | WEST ROW CSO HP008 | 6NW801571 | 254/1810 | 254/1810 |  | SO on sewer network | NZ4916127222 | GB103025076030 | Greatham Beck Catchment (trib of Tidal Tees) | GREATHAM BECK |  |  | Commissioned pre-2016 - full year data expected | 10.5 | 17 | 99.79%
Northumbrian Water | WEST SLEEKBURN FARM CSO | 6NW801294 | 226/1048 | 226/1048 |  | SO on sewer network | NZ2737784104 | GB103022076230 | Sleek Burn / Hepscott Burn Source to Tidal Limit | SLEEK BURN |  |  | Commissioned pre-2016 - full year data expected | 336 | 30 | 94.37%
Northumbrian Water | WEST STREET CSO | 6NW801305 | 243/0914 | 243/0914 |  | SO on sewer network | NZ2794036440 | GB103024077410 | Croxdale Beck from Source to Wear | BLAGDON BECK TRIB |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | WEST STREET P STN SSO | 6NW800620 | 254/E/0336 | 254/E/0336 |  | Storm discharge at pumping station | NZ4200013000 | GB103025072595 | Tees from Skerne to Tidal Limit | TEES |  |  | Commissioned in 2020 - full year data expected | 36.4744 | 8 | 100%
Northumbrian Water | WEST VIEW CSO | 6NW801151 | 235/1317 | 235/1317 |  | SO on sewer network | NZ2257663072 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 6.6333 | 10 | 100%
Northumbrian Water | KING OSWY DRIVE CSO WEST VIEW ROAD | 6NW801572 | 255/1116 | 255/1116 |  | SO on sewer network | NZ5001235871 | GB650301500005 | Tees Coastal | Culverted Watercourse |  |  | Commissioned pre-2016 - full year data expected | 2.5 | 6 | 99.99%
Northumbrian Water | WEST WOODBURN CSO | 6NW801496 | 255/1186 | 255/1186 |  | SO on sewer network | NZ3949636123 | GB103025075910 | Crimdon Beck from Source to Sea | TRIB. OF HEADS HOPE BURN |  |  | Commissioned pre-2016 - full year data expected | 29.25 | 16 | 96.67%
Northumbrian Water | WEST WOODBURN PUMPING STATION | 6NW800493 | 231/0966 | 231/0966 | 231/0966-01 | Storm discharge at pumping station | NY8927086790 | GB103023075320 | Rede from Bellshiel Burn to N Tyne | REDE |  |  | Commissioned in 2020 - full year data expected | 26.6783 | 10 | 99.18%
Northumbrian Water | WESTBOURNE DRIVE CSO | 6NW801412 | 245/1366 | 245/1366 |  | SO on sewer network | NZ3260252299 | GB103024077630 | Herrington Burn from Source to Lumley Park Burn | HERRINGTON BURN |  |  | Commissioned pre-2016 - full year data expected | 22.75 | 20 | 86.3% | Comms failure / issue | Resolved - May
Northumbrian Water | WESTERN AREA STW | 6NW800705 | 241/1146 | 241/1146 | 241/1146-02 | Storm tank at WwTW | NY9241037900 | GB103024077461 | Wear from Middlehope Burn to Houselop Beck | WEAR |  |  | Commissioned in 2020 - full year data expected | 697.305 | 74 | 100%
Northumbrian Water | WESTFIELD COURT CSO | 6NW801544 | 254/1921 | 254/1921 |  | SO on sewer network | NZ4317520372 | GB103025072550 | Lustrum Beck Catchment (trib of Tees) | LUSTRUM BECK TRIBUTARY |  |  | Commissioned pre-2016 - full year data expected | 2.5 | 7 | 97.02%
Northumbrian Water | WESTFIELD NO 9 PS | 6NW800839 | 210/0983 | 210/0983 | 210/0983-02 | SO on sewer network | NT9962354112 | 359 | #N/A | UNNAMED COASTAL STREAM |  |  | Commissioned pre-2016 - full year data expected | 4.5 | 5 | 79.15% | Comms failure / issue | Resolved - March
Northumbrian Water | WESTGATE CARAVAN SITE CSO | 6NW801680 | 241/1064 | 241/1064 |  | SO on sewer network | NY9074238028 | GB103024077461 | Wear from Middlehope Burn to Houselop Beck | WEAR |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 85.13% | Sensor failure / issue | N/A - Ongoing investigation
Northumbrian Water | WESTGATE CSO | 6NW800223 | 241/E/0471 | 241/E/0471 |  | SO on sewer network | NY9128038065 | GB103024077461 | Wear from Middlehope Burn to Houselop Beck | RIVER WEAR |  |  | Commissioned in 2016 - full year data expected | 131.75 | 27 | 99.99%
Northumbrian Water | WESTLINE INDUSTRIAL ESTATE CSO | 6NW801237 | 235/1872 | 235/1872 |  | SO on sewer network | NZ2648055681 | GB103023075670 | Team from Source to Tyne | ROWLETCH BURN |  |  | Commissioned pre-2016 - full year data expected | 4.25 | 2 | 99.98%
Northumbrian Water | WHALTON STW | 6NW800725 | 226/0927 | 226/0927 | B | Storm tank at WwTW | NZ1242480796 | GB103022076940 | How Burn from Source to Blyth | HOW BURN |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | WHESSOE SPS | 6NW800559 | 253/0053 | 253/0053 | A1 | Storm discharge at pumping station | NZ2940017800 | GB103025072596 | Skerne from Demons Beck to Tees | SKERNE, TRIBUTARY OF |  |  | Commissioned in 2020 - full year data expected | 29.3428 | 10 | 100%
Northumbrian Water | WHICKHAM SOUTH & SUNNISIDE CSO | 6NW801120 | 235/1966 | 235/1966 |  | SO on sewer network | NZ2101059990 | GB103023075670 | Team from Source to Tyne | TRIB BLACK BURN VIA SW SEWER |  |  | Commissioned pre-2016 - full year data expected | 2 | 2 | 99.99%
Northumbrian Water | WHISKEY JACKS PUMPING STATION | 6NW800508 | 234/1174 | 234/1174 | 234/1174-02 | Storm discharge at pumping station | NZ1585057741 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | DERWENT, RIVER |  |  | Commissioned in 2020 - full year data expected | 25.1436 | 17 | 100%
Northumbrian Water | WHITBURN STORM SEWAGE OVERFLOW | 6NW801516 | 245/1106 | 245/1106 |  | SO on sewer network | NZ4097061410 | GB650301500002 | Tyne and Wear | NORTH SEA |  | Seaburn (Whitburn North) | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.95%
Northumbrian Water | WHITBURN STEEL PS | 6NW800619 | 245/1207 | 245/1207 | 245/1207-01 | Storm discharge at pumping station | NZ4206061150 | GB650301500002 | Tyne and Wear | NORTH SEA |  | Seaburn (Whitburn North) | Commissioned in 2020 - full year data expected | 118.9492 | 31 | 94.39%
Northumbrian Water | WHITE STREET STATION ROAD CSO | 6NW800351 | 235/1329 | 235/1329 |  | SO on sewer network | NZ2981264400 | GB510302310200 | TYNE | RIVER TYNE ESTUARY |  |  | Commissioned in 2019 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | WHITE STREET STATION ROAD CSO | 6NW800350 | 235/1330 | 235/1330 |  | SO on sewer network | NZ2981264383 | GB510302310200 | TYNE | RIVER TYNE ESTUARY |  |  | Commissioned in 2019 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | WHITE HOUSE ROAD 1+2 CSO | 6NW801563M2 | 254/1823 | 254/1823 | 254/1823-1.3.1 | SO on sewer network | NZ4515024010 | GB103025076010 | Billingham Beck from Brierley Beck to Tees Es | THORPE BECK, TRIB OF BILL.BECK |  |  | Commissioned pre-2016 - full year data expected | 0.25 | 1 | 99.99%
Northumbrian Water | WHITE HOUSE ROAD 1+2 CSO | 6NW801563M3 | 254/1823 | 254/1823 | 254/1823-1.3.2 | SO on sewer network | NZ4515024010 | GB103025076010 | Billingham Beck from Brierley Beck to Tees Es | THORPE BECK, TRIB OF BILL.BECK |  |  | Commissioned pre-2016 - full year data expected | 32.5 | 44 | 99.98%
Northumbrian Water | WHITE-LE-HEAD ALLOTMENTS SSO | 6NW801050 | 235/1539 | 235/1539 |  | SO on sewer network | NZ1720754317 | GB103023075670 | Team from Source to Tyne | KYO BURN TRIB |  |  | Commissioned pre-2016 - full year data expected | 14.75 | 6 | 99.98%
Northumbrian Water | WHITTINGHAM STW | 6NW800691 | 222/0864 | 222/0864 | 222/0864-04 | Storm tank at WwTW | NU0716012080 | GB103022076310 | Aln from Callaly Burn to Coe Burn | RIVER ALN |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | WHITTLE COLLIERY VILLAGE STW | 6NW800693 | 223/0832 | 223/0832 |  | Storm tank at WwTW | NU1745706615 | GB103022076710 | Hazon Burn Catchment (trib of Coquet) | The Ogle Letch |  |  | April 2021 | 28.8186 | 9 | 100%
Northumbrian Water | WHORLTON STW | 6NW800718 | 25/02/1087 | 25/02/1087 | 25/02/1087-03 | Storm tank at WwTW | NZ1089014480 | GB103025072190 | Tees from River Greta to River Skerne | RIVER TEES |  |  | Commissioned in 2020 - full year data expected | 33.7269 | 12 | 99.41%
Northumbrian Water | WIDDRINGTON CSO | 6NW801222 | 224/0995 | 224/0995 |  | SO on sewer network | NZ2570493603 | GB103022076820 | Lyne from Source to Tidal Limit | LINTON BURN (RIVER LYNE) |  |  | Commissioned pre-2016 - full year data expected | 1.4667 | 4 | 100%
Northumbrian Water | WILLIAM STREET CSO | 6NW801394 | 235/1746 | 235/1746 |  | SO on sewer network | NZ3063565667 | GB510302310200 | TYNE | RIVER TYNE SALINE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 3 | 4 | 99.71%
Northumbrian Water | WILLIAM STREET CSO | 6NW801063 | 245/1266 | 245/1266 |  | SO on sewer network | NZ1896051840 | GB510302310200 | TYNE | TRIB OF STANLEY BURN |  |  | Commissioned pre-2016 - full year data expected | 0.5 | 2 | 99.99%
Northumbrian Water | WILLINGTON SYSTEM CSO | 6NW801076 | 243/D/0393 | 243/D/0393 |  | SO on sewer network | NZ1900031900 | GB103024077464 | Wear from Gaunless to Browney | WEAR, TRIBUTARY OF |  |  | Commissioned pre-2016 - full year data expected | 62.25 | 32 | 99.9%
Northumbrian Water | WILLINGTON STW | 6NW800746 | 243/0968 | 243/0968 | 243/0968-03 | Storm tank at WwTW | NZ2109034460 | GB103024077464 | Wear from Gaunless to Browney | WEAR |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | WILLOW BRIDGE CSO | 6NW801219 | 226/1239 | 226/1239 |  | SO on sewer network | NZ2567083650 | GB103022076230 | Sleek Burn / Hepscott Burn Source to Tidal Limit | THE SLEEK BURN |  |  | Commissioned pre-2016 - full year data expected | 144.5 | 41 | 99.98%
Northumbrian Water | WINCOMBLEE B PUMPING STATION | 6NW800565 | 235/1757 | 235/1757 | Sch 1/3 | Storm discharge at pumping station | NZ2980064270 | GB510302310200 | TYNE | RIVER TYNE SALINE ESTUARY |  |  | Commissioned in 2018 - full year data expected | 2.5483 | 5 | 99.84%
Northumbrian Water | WINCOMBLEE C PUMPING STATION | 6NW800564 | 235/1758 | 235/1758 |  | Storm discharge at pumping station | NZ2982064390 | GB510302310200 | TYNE | RIVER TYNE SALINE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 142.5 | 29 | 97.93%
Northumbrian Water | WINCOMBLEE ROAD CSO | 6NW800352 | 235/1759 | 235/1759 |  | SO on sewer network | NZ2981264400 | GB510302310200 | TYNE | RIVER TYNE SALINE ESTUARY |  |  | Commissioned in 2019 - full year data expected | 104.25 | 35 | 87.26% | Sensor failure / issue | Resolved - August
Northumbrian Water | WINDLESTONE STW | 6NW800771 | 253/1269 | 253/1269 | A2 | Storm tank at WwTW | NZ2899028590 | GB103025072450 | Rushyford Beck from Source to Woodham Burn | RUSHYFORD BECK, TRIBUTARY OF |  |  | Commissioned in 2020 - full year data expected | 1392.6797 | 89 | 99.99%
Northumbrian Water | WINDMILL COTTAGE CSO THE MILL TE066 | 6NW800921 | 252/1125 | 252/1125 |  | SO on sewer network | NZ0151019565 | GB103025072511 | Tees from Maize Beck to Percy Beck | UNNAMED TRIB OF LANCE BECK |  |  | Commissioned pre-2016 - full year data expected | 24.1 | 11 | 89.96% | Comms failure / issue | Resolved - October
Northumbrian Water | WINGATE CSO NO 1 | 6NW801488 | 255/E/0642 | 255/E/0642 |  | SO on sewer network | NZ3784436372 | GB103025076070 | Skerne from Source to Carrs | River Skerne |  |  | Commissioned pre-2016 - full year data expected | 2.75 | 7 | 84.58% | Comms failure / issue | Resolved - December
Northumbrian Water | WINSTON STW SSO | 6NW800152 | 25/02/1104 | 25/02/1104 | 25/02/1104-01 | Inlet SO at WwTW | NZ1433016540 | GB103025072190 | Tees from River Greta to River Skerne | RIVER TEES |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Northumbrian Water | WITTON GILBERT STW | 6NW801159 | 244/0889 | 244/0889 |  | SO on sewer network | NZ2328145066 | GB103024077551 | Browney from Smallhope Burn Deerness confl | RIVER BROWNEY |  |  | Commissioned pre-2016 - full year data expected | 367 | 78 | 99.26% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | WITTON GILBERT STW | 6NW800753 | 244/1027 | 244/1027 | 244/1027-02 | Storm tank at WwTW | NZ2328045067 | GB103024077551 | Browney from Smallhope Burn Deerness confl | River Browney |  |  | Commissioned in 2020 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | WOOD GROVE CSO (NC029) | 6NW801093 | 235/1939 | 235/1939 |  | SO on sewer network | NZ1965463974 | GB510302310200 | TYNE | RIVER TYNE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 124.0667 | 56 | 86.25% | Comms failure / issue | Resolved - July | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
Northumbrian Water | WOODBOROUGH LANE CSO | 6NW801532 | 25/04/1607 | 25/04/1607 |  | SO on sewer network | NZ4293320382 | GB103025072550 | Lustrum Beck Catchment (trib of Tees) | ELM TREE BECK |  |  | Commissioned pre-2016 - full year data expected | 1.5 | 2 | 99.99%
Northumbrian Water | WOODFIELD HILL CROOK CSO | 6NW801006 | EPRBB3499RX | EPRBB3499RX |  | SO on sewer network | NZ1510235246 | GB103024077390 | Beechburn Beck (Trib of Wear) | CULVERTED BEECHBURN BECK |  |  | Commissioned pre-2016 - full year data expected | 0.25 | 1 | 94.02%
Northumbrian Water | WOODFORD NO 22 STORM OVERFLOW | 6NW801239 | 235/1520 | 235/1520 |  | SO on sewer network | NZ2544058540 | GB103023075670 | Team from Source to Tyne | TEAM TRIB |  |  | Commissioned pre-2016 - full year data expected | 44.25 | 43 | 96.8%
Northumbrian Water | WOODGATE GDNS/MARCONI 2 CSO | 6NW801345 | 235/1981 | 235/1981 |  | SO on sewer network | NZ2919062941 | GB510302310200 | TYNE | TYNE ESTUARY |  |  | Commissioned pre-2016 - full year data expected | 0.5 | 1 | 99.77%
Northumbrian Water | WOODHOUSE LANE LIBRARY CSO | 6NW801678 | EPRBB3093WE | EPRBB3093WE |  | SO on sewer network | NZ2101027823 | GB103024072730 | Gaunless from Hummer Beck to Wear | RIVER GAUNLESS |  |  | Commissioned in 2016 - full year data expected | 4 | 8 | 99.99%
Northumbrian Water | WOODLAND VIEW CSO | 6NW801497 | 255/1184 | 255/1184 |  | SO on sewer network | NZ3994037490 | GB103025075910 | Crimdon Beck from Source to Sea | TRIB. OF HEADS HOPE BURN |  |  | Commissioned pre-2016 - full year data expected | 2.75 | 7 | 99.75%
Northumbrian Water | WARKWORTH PUMPING STATION NO3 WOODLANDS | 6NW800475 | 223/B/0223 | 223/B/0223 | A1 | Storm discharge at pumping station | NU2490005700 | GB510302203000 | COQUET | COQUET |  | Warkworth & Amble Links | Commissioned pre-2016 - full year data expected | 8.8667 | 3 | 40.09% | Comms failure / issue | Scheduled
Northumbrian Water | WOODLANDS PUMPING STATION | 6NW800496 | 233/1065 | 233/1065 | A | Storm discharge at pumping station | NY9494063930 | GB103023075801 | Tyne from Watersmeet to Tidal Limit | RIVER TYNE TRIBUTARY |  |  | Commissioned in 2020 - full year data expected | 131.2831 | 25 | 89.43% | Sensor failure / issue | Resolved - April
Northumbrian Water | WOODWYND CSO | 6NW801342 | 235/A/0508 | 235/A/0508 |  | SO on sewer network | NZ2925059760 | GB103023075690 | Don from Source to Tidal Limit | DON |  |  | Commissioned pre-2016 - full year data expected | 57.75 | 11 | 99.51%
Northumbrian Water | WOOLER SPS | 6NW800456 | 210/0970 | 210/0970 | A1 | Storm discharge at pumping station | NT9945028530 | GB102021072930 | Wooler Water from Harthope Burn to Till | WOOLER WATER |  |  | Commissioned in 2019 - full year data expected | 71.4244 | 13 | 99.44%
Northumbrian Water | WOOLER STW | 6NW800107 | 210/1275 | 210/1275 | A2 | Inlet SO at WwTW | NT9990629453 | GB102021072930 | Wooler Water from Harthope Burn to Till | WOOLER WATER |  |  | Commissioned in 2019 - full year data expected | 218.5275 | 20 | 16.64% | Installation set-up/design issue | Resolved - November
Northumbrian Water | WOOLSINGTON CSO | 6NW801095 | EPRCB3191ED | EPRCB3191ED |  | SO on sewer network | NZ1961469983 | GB103023075780 | Ouse Burn from Source to Tyne | OUSE BURN |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 97.85%
Northumbrian Water | WORKINGMEN'S CLUB CSO | 6NW801444 | 243/1004 | 243/1004 |  | SO on sewer network | NZ3406036020 | GB103024077410 | Croxdale Beck from Source to Wear | COXHOE BECK |  |  | Commissioned pre-2016 - full year data expected | 0.25 | 1 | 99.87%
Northumbrian Water | BRANCEPETH CSO | 6NW801147 | EPRBB3990WL | EPRBB3990WL |  | SO on sewer network | NZ2240337542 | GB103024077420 | Brancepeth Beck from Source to Wear | STOCKLEY BECK |  |  | Commissioned pre-2016 - full year data expected | 1.5 | 4 | 42.58% | Comms failure / issue | Resolved - November
Northumbrian Water | WORMHILL TERRACE CSO | 6NW801367 | 245/1303 | 245/1303 |  | SO on sewer network | NZ3091754093 | 9 | #N/A | BIDDICK BURN |  |  | Commissioned pre-2016 - full year data expected | 0.16667 | 1 | 100%
Northumbrian Water | WORSALL ROAD PUMPING STATION | 6NW800621 | 25/04/1648 | 25/04/1648 | 25/04/1648-01 | Storm discharge at pumping station | NZ4174012250 | GB103025072595 | Tees from Skerne to Tidal Limit | SKYTERING BECK (R.TEES CATCH) |  |  | Commissioned in 2020 - full year data expected | 107.8361 | 21 | 100%
Northumbrian Water | YARM BRIDGE CSO | 6NW801517 | 254/1178 | 254/1178 |  | SO on sewer network | NZ4180413187 | GB103025072595 | Tees from Skerne to Tidal Limit | RIVER TEES |  |  | Commissioned pre-2016 - full year data expected | 2.25 | 8 | 99.99%
Northumbrian Water | YARM ROAD CSO (Y2) | 6NW801328 | EPRMB3892EJ | EPRMB3892EJ |  | SO on sewer network | NZ2912514232 | GB103025072596 | Skerne from Demons Beck to Tees | RIVER SKERNE |  |  | Commissioned pre-2016 - full year data expected | 1.5 | 4 | 99.82%
Northumbrian Water | YARM ROAD CSO (Y3) | 6NW801357 | EPRMB3892RF | EPRMB3892RF |  | SO on sewer network | NZ2912514232 | GB103025072596 | Skerne from Demons Beck to Tees | RIVER SKERNE |  |  | Commissioned pre-2016 - full year data expected | 19.25 | 22 | 99.57%
Northumbrian Water | YARM ROAD CSO (Y6) | 6NW801331 | EPRMB3892VE | EPRMB3892VE |  | SO on sewer network | NZ2912514232 | GB103025072596 | Skerne from Demons Beck to Tees | RIVER SKERNE |  |  | Commissioned pre-2016 - full year data expected | 0.75 | 1 | 84.44% | Sensor failure / issue | Scheduled
Northumbrian Water | YARM ROAD / MUIRFIELD ROAD CSO | 6NW801526 | EPRCB3195EM | EPRCB3195EM |  | SO on sewer network | NZ4233314833 | GB103025072595 | Tees from Skerne to Tidal Limit | TRIB OF RIVER TEES |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 79.57% | Sensor failure / issue | Resolved - December
Northumbrian Water | YORK HILL CSO | 6NW800543 | 243/1010 | 243/1010 | 243/1010-02 | Storm discharge at pumping station | NZ2740035700 | GB103024077464 | Wear from Gaunless to Browney | NICKYNACK BECK |  |  | Commissioned in 2020 - full year data expected | 0 | 0 | 100%
Northumbrian Water | ZETLAND ROW CSO | 6NW801647 | 256/1076 | 256/1076 |  | SO on sewer network | NZ7137519883 | GB103025071950 | Kilton Beck from Middle Gill Beck to North Sea | SKINNINGROVE BECK (KILTON B.) |  |  | Commissioned pre-2016 - full year data expected | 4.75 | 3 | 99.98%
Northumbrian Water | SNOWDONS FARM CSO | 6NW800312 | 244/1000 | 244/1000 |  | SO on sewer network | NZ2586040040 | GB103024077552 | Browney from Deerness confl to Wear | River Browney |  |  | EDM to be installed by December 2023 | #N/A | #N/A | #N/A
Northumbrian Water | GENEVA ROAD CSO | 6NW801356(2) | 254/1908 | 254/1908 |  | SO on sewer network | NZ3069012933 | GB103025072160 | Neasham Stell Catchment (trib of Tees) | Cree Beck into Kent Beck |  |  | EDM to be installed by December 2023 | #N/A | #N/A | #N/A
Northumbrian Water | HORDEN DENE SSO NO 1 OAK ROAD | 6NW000013 | 255/E/0644 | 255/E/0644 |  | SO on sewer network | NZ4238643364 | 367 | #N/A | Culverted watercourse to Thorpe Burn |  |  | Commissioned in 2017 - full year data expected | #N/A | #N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
Northumbrian Water | VINOVIUM SSO NO A23 ATHERTON TERRACE | 6NW000014 | 242/C/0381 | 242/C/0381 |  | SO on sewer network | NZ2201028387 | GB103024072730 | Gaunless from Hummer Beck to Wear | Dene Beck |  |  | EDM to be installed by December 2023 | #N/A | #N/A | #N/A
Northumbrian Water | MARSKE SEWAGE TREATMENT WORKS | 6NW800203(1) | 25/06/1015 | 25/06/1015 |  | Inlet SO at WwTW | NZ6405024199 | GB650301500005 | Tees Coastal | North Sea |  | Marske | Commissioned in 2020 - full year data expected | 0.026111 | 2 | 100%
Northumbrian Water | TOWER ROAD CSO | 6NW000015 | #TBC | Permit Anomaly | To be permitted for storm | SO on sewer network | NT9973552213 | GB510202110000 | TWEED | River Tweed |  | Spittal | Commissioned pre-2016 - full year data expected | 0.23333 | 4 | 99.99%
Northumbrian Water | WELLINGTON ROAD CSO (E9-102) | 6NW800280 | #TBC | Permit Anomaly | To be permitted for storm | SO on sewer network | NZ2224662911 | 8 | #N/A | River Tyne |  |  | Commissioned in 2020 - full year data expected | 835.405 | 59 | 98.57%
Northumbrian Water | GUISBOROUGH STW OVERFLOW | 6NW800803 | 25/06/1021 | 25/06/1021 | 25/06/1021-01 | SO on sewer network | NZ5998016100 | GB103025071970 | Skelton Beck Catch (Saltburn) trib of North Sea | CHAPEL BECK - HOWL BECK SYSTEM |  | Saltburn Pier | EDM to be installed by December 2023 | #N/A | #N/A | #N/A
Northumbrian Water | SEVENTH AVENUE CSO | 6NW801209 | 235/F/0652 | 235/F/0652 |  | SO on sewer network | NZ2462059510 | GB103023075670 | Team from Source to Tyne | River Team |  |  | EDM to be installed by December 2023 | #N/A | #N/A | #N/A
Northumbrian Water | STATION ROAD/SWAN HUNTERS CSO | 6NW800573 | 235/1597 | 235/1597 |  | SO on sewer network | NZ3033665764 | 8 | #N/A | River Tyne |  |  | June 2021 | 35.1078 | 27 | 99.26%
Northumbrian Water | STATION ROAD/WHITE STREET CSO | 6NW000016 | EPRCB3797VZ | EPRCB3797VZ |  | SO on sewer network | NZ2981264383 | GB510302310200 | TYNE | River Tyne |  |  | Commissioned in 2019 - full year data expected | 2 | 2 | 99.23%
Northumbrian Water | CRAWCROOK LANE CSO | 6NW000017 | 233/1258 | 233/1258 |  | SO on sewer network | NZ1305265096 | 8 | #N/A | River Tyne |  |  | EDM to be installed by December 2023 | #N/A | #N/A | #N/A
Northumbrian Water | ALNWICK GARDENS CSO | 6NW000018 | #TBC | Permit Anomaly | To be permitted for storm | SO on sewer network | NU1925913393 | GB103022076350 | Aln from Edlingham Burn to Tidal Limit | Culverted Watercourse to River Aln |  |  | EDM to be installed by December 2023 | #N/A | #N/A | #N/A
Northumbrian Water | DARLINGTON CSO | 6NW000019 | #TBC | Permit Anomaly | To be permitted for storm | SO on sewer network | NZ4309417998 | GB103025072550 | Lustrum Beck Catchment (trib of Tees) | Lustrum Beck |  |  | Commissioned in 2019 - full year data expected | 10.5 | 16 | 99.99%
Northumbrian Water | BELFORD STREET CSO | 6NW000020 | #TBC | Permit Anomaly | To be permitted for storm | SO on sewer network | NZ4387442111 | 367 | #N/A | Unnamed watercourse |  |  | Commissioned in 2019 - full year data expected | 15 | 19 | 99.82%
Northumbrian Water | MILFIELD CSO | 6NW000021 | #TBC | Permit Anomaly | To be permitted for storm | SO on sewer network | NT9380734319 | GB102021073050 | Till from Glen to River Tweed | Unnamed Trib River Till |  |  | Commissioned pre-2016 - full year data expected | 126 | 37 | 99.97%
Northumbrian Water | COLLINGWOOD TERRACE CSO | 6NW000022 | #TBC | Permit Anomaly | To be permitted for storm | SO on sewer network | NZ3694368873 / NZ3694268961 | 8 | #N/A | River Tyne |  |  | Commissioned pre-2016 - full year data expected | 21.5 | 22 | 99.79%
Northumbrian Water | PLAWSWORTH GATE CSO | 6NW000023 | #TBC | Permit Anomaly | To be permitted for storm | SO on sewer network | NZ2632347177 | GB103024077622 | Blackdene Burn to confluence with Wear | Blackdene Burn |  |  | Commissioned pre-2016 - full year data expected | 234 | 52 | 99.56%
Northumbrian Water | MURTON CSO 15 | 6NW000024 | #TBC | Permit Anomaly | To be permitted for storm | SO on sewer network | NZ3845046638 | GB103025075970 | Dalton Beck to North Sea | Unnamed watercourse |  |  | Commissioned pre-2016 - full year data expected | 23.75 | 20 | 99.99%
Northumbrian Water | PALLION CSO 4 | 6NW000025 | #TBC | Permit Anomaly | To be permitted for storm | SO on sewer network | NZ3899757745 | GB510302402900 | WEAR | River Wear |  |  | Commissioned pre-2016 - full year data expected | 87 | 54 | 99.99%
Northumbrian Water | MARLEY HILL SPS | 6NW000026 | #TBC | Permit Anomaly | To be permitted for storm | Storm discharge at pumping station | NZ2011657283 | GB103023075670 | Team from Source to Tyne | Cultivated watercourse to Bobkins Burn |  |  | EDM to be installed by December 2023 | #N/A | #N/A | #N/A
Northumbrian Water | SOUTH ROAD UPPER CSO | 6NW000027 | #TBC | Permit Anomaly | To be permitted for storm | SO on sewer network | NZ1646227588 | GB103024072690 | Gaunless from Source to Hummer Beck | Unnamed watercourse |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 81.93% | Comms failure / issue | Scheduled
Northumbrian Water | SOUTH ROAD LOWER CSO | 6NW000028 | #TBC | Permit Anomaly | To be permitted for storm | SO on sewer network | NZ1646227588 | GB103024072690 | Gaunless from Source to Hummer Beck | Unnamed watercourse |  |  | Commissioned pre-2016 - full year data expected | 0.5 | 1 | 75.52% | Comms failure / issue | Resolved - November
Northumbrian Water | BUTTERKNOWLE CSO 2 | 6NW000029 | #TBC | Permit Anomaly | To be permitted for storm | SO on sewer network | NZ1148325442 | GB103024072690 | Gaunless from Source to Hummer Beck | River Gaunless |  |  | Commissioned in 2019 - full year data expected | 311.4167 | 63 | 79.16% | Access - Unable to retrieve data from non-telemetry data logger (NB: not to be used for delayed access to fix existing fault) | Scheduled
Northumbrian Water | PORT CLARENCE EAST PUMPING STATION | 6NW000030 | 254/1948 | 254/1948 | A1 | Storm discharge at pumping station | NZ5016221387 | GB510302509900 | TEES | River Tees |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 96.25%
Northumbrian Water | ELWICK SPS | 6NW800634(2) | 254/1076 | 254/1076 | A1 | Storm discharge at pumping station | NZ4570232085 | GB103025076030 | Greatham Beck Catchment (trib of Tidal Tees) | CHAR BECK |  |  | EDM to be installed by December 2023 | #N/A | #N/A | #N/A
Northumbrian Water | HAWTHORN STW | 6NW000031 | 255/1220 | 255/1220 | 255/1220-02 | Storm tank at WwTW | NZ4269045615 | GB103025075950 | Hawthorn Burn from Source to North Sea | North Dene Burn |  |  | EDM to be installed by December 2023 | #N/A | #N/A | #N/A
Northumbrian Water | WOLSINGHAM STW | 6NW000032 | 241/1102 | 241/1102 | A2 | Storm tank at WwTW | NZ1066035647 | GB103024077462 | Wear from Houselop Beck to Beechburn Beck | River Wear |  |  | EDM to be installed by December 2023 | #N/A | #N/A | #N/A
Northumbrian Water | Holburn Lane CSO, Ryton - NWL name | 6NW000040 | #TBC | Permit Anomaly | To be permitted for storm | SO on sewer network | NZ1589665285 | GB510302310200 | TYNE | River Tyne estuary |  |  | EDM to be installed by December 2023 | #N/A | #N/A | #N/A
Northumbrian Water | Dunelm Road CSO DER 147 - NWL name | 6NW000052 | #TBC | Permit Anomaly | To be permitted for storm | SO on sewer network | NZ0909049645 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | River Derwent via road drain |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.26%
Northumbrian Water | CONSETT CSO DERWENTDALE INDUSTRIAL ESTATE DER 168 (OOS) - NWL name | 6NW000051 | #TBC | Permit Anomaly | To be permitted for storm | SO on sewer network | NZ0914150934 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | culverted section of Howden Burn |  |  | Commissioned pre-2016 - full year data expected | 291.5 | 31 | 99.99%
Northumbrian Water | CONSETT LOW WOOD NORTH - NWL name | 6NW000034 | #TBC | Permit Anomaly | To be permitted for storm | SO on sewer network | NZ08866 50067 | GB103023074790 | Derwent from Burnhope Burn to River Tyne | Tributary of Dene Burn (River Derwent) |  |  | Commissioned in 2017 - full year data expected | 0 | 0 | 96.75%
Northumbrian Water | Manhole off Durham Road (Next to Sorrento Pizza shop) - NWL name | 6NW000035 | #TBC | Permit Anomaly | To be permitted for storm | SO on sewer network | NZ2678255278 | GB103023075670 | Team from Source to Tyne | Rowletch Burn |  |  | Commissioned in 2019 - full year data expected | 0.75 | 1 | 99.99%
Northumbrian Water | SOUTH MOOR CSO CHARLES STREET DER066 - NWL name | 6NW000037 | #TBC | Permit Anomaly | To be permitted for storm | SO on sewer network | NZ1923451825 (to a culverted watercourse which opens at NZ1972351654) | GB103024077590 | Twizell Burn from Source to Cong Burn | Culverted tributary of the Stanley Burn |  |  | Commissioned pre-2016 - full year data expected | 1.25 | 1 | 99.99%
Northumbrian Water | WASHINGTON CSO DON GARDENS - NWL name | 6NW000038 | #TBC | Permit Anomaly | To be permitted for storm | SO on sewer network | NZ3102858090 | GB103023075690 | Don from Source to Tidal Limit | Culverted tributary of the River Don |  |  | Commissioned pre-2016 - full year data expected | 52.75 | 17 | 99.98%
Northumbrian Water | Dukes Walk CSO | 6NW000044 | 235/1798 | 235/1798 |  | SO on sewer network | NZ3518073399 | GB650301500002 | Tyne and Wear | North Sea |  |  | EDM to be installed by December 2023 | #N/A | #N/A | #N/A
Northumbrian Water | MARINER S WHARF, QUAYSIDE - NWL name | 6NW000041 | #TBC | Permit Anomaly | modellling indicates operation >1:30 permit requirement | SO on sewer network | NZ2633864110 | GB510302310200 | Tyne | River Tyne Estuary |  |  | EDM to be installed by December 2023 | #N/A | #N/A | #N/A
Northumbrian Water | NEPTUNE YARD CSO - NWL name | 6NW000042 | #TBC | Permit Anomaly | To be permitted for storm | SO on sewer network | NZ3000765386 | 8 | #N/A | River Tyne Estuary |  |  | EDM to be installed by December 2023 | #N/A | #N/A | #N/A
Northumbrian Water | Little Coop House Farm - NWL name | 6NW000043 | #TBC | Permit Anomaly | To be permitted for storm | SO on sewer network | NZ3984445859 | GB103025075970 | Dalton Beck to North Sea | Culverted section of Coop House Beck |  |  | EDM to be installed by December 2023 | #N/A | #N/A | #N/A
Northumbrian Water | Tursdale PS - NWL name | 6NW000045 | #TBC | Permit Anomaly | To be permitted for storm | Storm discharge at pumping station | NZ3011935485 | GB103024077410 | Croxdale Beck from Source to Wear | Coxhoe Beck |  |  | EDM to be installed by December 2023 | #N/A | #N/A | #N/A
Northumbrian Water | Allotment Gardens, Shotton Colliery - NWL name | 6NW000039 | #TBC | Permit Anomaly | To be permitted for storm | SO on sewer network | NZ3962641208 | GB103025075930 | Castle Eden Burn from Source to North Sea | TBC |  |  | August 2021 | 0 | 0 | 98.99%
Northumbrian Water | Alwinton STW | 6NW000046M2 | 223/0419 |  |  | Inlet SO at WwTW | NT9205006166 | GB103022076770 | Alwin Catchment (trib of Coquet) | Hosedon Burn tributary of River Coquet |  |  | Commissioned in 2019 - full year data expected | 21.5003 | 13 | 79.44% | Comms failure / issue | N/A - Ongoing investigation
Northumbrian Water | Alwinton STW | 6NW000046M3 | 223/0419 |  |  | Inlet SO at WwTW | NT9205006166 | GB103022076770 | Alwin Catchment (trib of Coquet) | Hosedon Burn tributary of River Coquet |  |  | Commissioned in 2019 - full year data expected | 321.0006 | 49 | 35.29% | Comms failure / issue | N/A - Ongoing investigation
Northumbrian Water | Saltburn Bank CSO NWL name | 6NW000047 | #TBC | Permit Anomaly | To be permitted for storm | SO on sewer network | NZ6677721617 | GB650301500005 | Tees Coastal Water Body | Skelton Beck |  |  | Commissioned pre-2016 - full year data expected | 12.3667 | 3 | 100%
Northumbrian Water | Scottswood Road (C49-104) NWL name | 6NW000036 | #TBC | Permit Anomaly | To be permitted for storm | SO on sewer network | NZ2207663278 | GB510302310200 | TYNE | River Tyne |  |  | Commissioned pre-2016 - full year data expected | 0.75 | 3 | 85.96% | Comms failure / issue | Resolved - August
Northumbrian Water | Heugh Hall Row STW NWL name | 6NW000049 | 243/0092 | Permit Anomaly - STW permit 243/0092 |  | Inlet SO at WwTW | NZ3124337712 | GB103024077410 | Croxdale Beck from Source to Wear | Tributary of Bowburn Beck |  |  | EDM to be installed by December 2023 | #N/A | #N/A | #N/A
Northumbrian Water | Scotswood Road CSO (C43-105) NWL name | 6NW000048 | #TBC | Permit Anomaly |  | SO on sewer network | NZ2322062914 | GB510302310200 | Tyne | River Tyne |  |  | Commissioned pre-2016 - full year data expected | 0 | 0 | 99.99%
Note on D423: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 25/06/1018 (New Marske Methodist Church) on Consents Database has same NGR
Note on D989: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 255/5014 (BRENDA ROAD/PARK VIEW CSO) on Consents Database has same NGR
Note on D1056: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 254/0663 (Teesbank Avenue CSO) on Consents Database has same NGR

## Drop Downs - SO
Storm discharge asset type | Initial EDM Commission Date | EDM Operation - Reporting percentage - Primary Reason <90% | EDM Operation - Action taken / planned - Status & Timeframe | High Spill Frequency - Operational Review - Primary Reason (Asset Maintenance) | High Spill frequency - Action taken / planned - Status & Timeframe | High Spill Frequency - Environmental Enhancement - Planning Position (Hydraulic Capacity)
SO on sewer network | Installed but not yet commissioned | Access - Unable to retrieve data from non-telemetry data logger (NB: not to be used for delayed access to fix existing fault) | Scheduled | Performance - Partial / no capacity due to blockage or restriction (e.g. roots / grid) - maintenance issue | Scheduled | SOAF N/A - Proposed SFTP (overflow previously improved)
Storm discharge at pumping station | Commissioned in 2020 - full year data expected | Capital / maintenance works affect EDM operation | Resolved - January | Performance - Sewer collapse (partial / full) - infrastructure issue | Resolved - January | Stage 1a: Confirmed "exceptional weather" issue
Inlet SO at WwTW | Commissioned in 2019 - full year data expected | Comms failure / issue | Resolved - Feburary | Performance - GW inundation | Resolved - Feburary | Stage 1b: Confirmed "asset maintenance" issue
Storm tank at WwTW | Commissioned in 2018 - full year data expected | EDM not yet installed | Resolved - March | Performance - Infiltration | Resolved - March | Stage 1c: Confirmed "hydraulic issue"
Other storm discharge asset type | Commissioned in 2017 - full year data expected | EDM installed - not yet commissioned | Resolved - April | Performance - Asset power failure | Resolved - April | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
| Commissioned in 2016 - full year data expected | Installation set-up/design issue | Resolved - May | Performance - Pump failure / issue | Resolved - May | U_INV driver - Stage 4: Cost beneficial outcome not yet determined
| Commissioned pre-2016 - full year data expected | Power failure / issue | Resolved - June | Performance - Other maintenance / capital works (e.g. jetting) | Resolved - June | U_INV driver - Stage 4: No cost beneficial solution
| Jan 2021 | Sensor failure / issue | Resolved - July | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | Resolved - July | U_IMP4 driver - Stage 4: Spill reduction scheme - On current WINEP/AMP7 or Green Recovery
| Feb 2021 | Telemetry or data archiving failure / issue | Resolved - August | Data collection - EDM non-representative location | Resolved - August | U_IMP4 driver - Stage 4: Potential spill reduction scheme - Not yet on current WINEP/AMP7 or Green Recovery
| Mar 2021 | No longer operational as an overflow - permit revoked or to be revoked | Resolved - September | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | Resolved - September | N/A - Operational solution applied
| April 2021 |  | Resolved - October | Data collection - Tidal / river inundation | Resolved - October
| May 2021 |  | Resolved - November | Not asset maintenance - Hydraulic capacity | Resolved - November
| June 2021 |  | Resolved - December |  | Resolved - December
| July 2021 |  | N/A - Ongoing investigation |  | N/A - Ongoing investigation
| August 2021 |  | N/A - EDM to be installed by December 2023 |  | N/A - Hydraulic capacity
September 2021
October 2021
November 2021
December 2021
EDM to be installed by December 2023